## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2024-12-06
This version is 607 days old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2023-12-04
This version is 975 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 0 | 11.6914 | 20.5513 | 3.5861 | 2.6279 | 11.6914 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 9.3464 | 16.0364 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0 | 3.3047 | 3.3047 | 3.3047 | 0 | 3.2626 | 1.1073 | PP submitted, offer due 16/01/2025
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 10.2776 | 29.6287 | 24.8274 | 17.8439 | 10.2776 | 0 | 0 | PP submitted, offer due 16/01/2025
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 3.9784 | 8.1154 | 32.3302 | 6.1925 | 4.5182 | 8.1154 | 4.8939 | 0.33304 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 6.3973 | 11.1473 | 19.2839 | 19.2839 | 15.5992 | 11.1473 | 15.7536 | 7.6053 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 3.782 | 9.282 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 4.9016 | 7.9016 | 21.7548 | 9.4792 | 6.9163 | 7.9016 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0.47844 | 5.4784 | 11.2179 | 1.9575 | 1.4344 | 5.4784 | 1.4344 | 0 | Offer signed 27/08/2024
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 10.2776 | 18.3845 | 18.3845 | 18.3845 | 10.2776 | 0 | 0 | PP submitted, offer due 16/01/2025
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 2.446 | 26.2485 | 8.5896 | 6.2672 | 2.446 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.9452 | 1.9452 | 5.57 | 1.9575 | 1.4344 | 1.9452 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 9.5983 | 13.7383 | 28.8941 | 8.5422 | 6.2327 | 13.7383 | 6.5315 | 13.4847 | N/A
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 4.9687 | 9.1057 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9141 | 11.6641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 2.2895 | 2.2895 | 31.4391 | 9.2369 | 6.7395 | 2.2895 | 1.3561 | 10.6051 | Offer signed 27/08/2024
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 1.548 | 8.528 | 11.7207 | 6.342 | 4.5581 | 8.528 | 6.4697 | 8.428 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92953 | 1.6295 | 3.9789 | 3.9789 | 3.9789 | 1.6295 | 3.9789 | 1.6295 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 3.5562 | 5.5562 | 7 | 1.9575 | 1.4344 | 5.5562 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 6.3779 | 6.5025 | 29.4311 | 4.8456 | 3.4826 | 6.5025 | 3.7461 | 0 | Offer with ENW, due to be signed 27/2/2024
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 5.3292 | 8.8292 | 22.71 | 13.1594 | 9.6015 | 8.8292 | 9.6723 | 7.1892 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 0.72949 | 0.72949 | 11.2179 | 1.9575 | 1.4344 | 0.72949 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 3.6678 | 8.3048 | 30.0013 | 9.7511 | 7.0083 | 8.3048 | 7.6584 | 8.6278 | N/A
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 4.8193 | 8.9563 | 11.2179 | 1.9575 | 1.4344 | 8.9563 | 1.4344 | 10.2623 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 3.3385 | 11.2179 | 1.9575 | 1.4344 | 3.3385 | 1.4344 | 9.8525 | Offer with ENW, due to be signed 27/2/2024
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.8644 | 18.3644 | 21.1384 | 9.6474 | 7.0695 | 18.3644 | 8.0292 | 18.3194 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 3.9941 | 10.2441 | 11.2179 | 1.9575 | 1.4344 | 10.2441 | 1.4344 | 10.2441 | N/A
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 5.2731 | 6.5025 | 28.5003 | 10.0852 | 7.2484 | 6.5025 | 7.2768 | 0 | Offer with ENW, due to be signed 27/2/2024
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.1244 | 10.6244 | 23.1258 | 11.104 | 8.1018 | 10.6244 | 9.5768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.8921 | 9.8921 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 9.8921 | PP submitted, offer due 12/12/2024
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 5.2812 | 7.259 | 7.259 | 7.259 | 5.2812 | 0 | 0 | PP submitted, offer due 16/01/2025
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 4.9191 | 9.5561 | 11.2179 | 1.9575 | 1.4344 | 9.5561 | 1.4344 | 10.1499 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 6.0841 | 10.2211 | 11.2179 | 1.9575 | 1.4344 | 10.2211 | 1.4344 | 6.4123 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 7.7664 | 12.4034 | 31.3792 | 9.2804 | 6.7712 | 12.4034 | 6.1854 | 10.7604 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 14.1134 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 11.043 | 15.68 | 30.3333 | 13.0966 | 9.5556 | 15.68 | 9.7958 | 15.68 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 13.535 | 21.285 | 33.7019 | 8.5909 | 6.2682 | 21.285 | 6.7082 | 17.439 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 0.51579 | 2.9381 | 11.2179 | 1.9575 | 1.4344 | 2.9381 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.2939 | 8.4802 | 8.4802 | 8.4802 | 4.2939 | 8.4802 | 3.8465 | Offer signed 20/11/2024
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.6138 | 10.6138 | 20.5557 | 20.5557 | 19.2116 | 10.6138 | 19.2177 | 9.8578 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 2.5751 | 7.2121 | 29.2513 | 6.1543 | 4.4232 | 7.2121 | 3.7567 | 5.6289 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 12.9879 | 33.4879 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 5.7917 | 10.4287 | 32.4374 | 12.2416 | 8.7983 | 10.4287 | 8.9022 | 10.8219 | N/A
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 4.5459 | 9.1829 | 11.2179 | 1.9575 | 1.4344 | 9.1829 | 1.4344 | 0 | Offer signed 27/08/2024
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 8.9885 | 19.6285 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 27/2/2024
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 3.7638 | 7.2638 | 24.6012 | 12.5946 | 9.052 | 7.2638 | 9.1136 | 8.37 | Offer with ENW, due to be signed 22/01/2025
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 4.976 | 13.7357 | 30.3079 | 13.2452 | 9.6641 | 13.7357 | 9.8568 | 6.6125 | PP submitted, offer due 12/12/2024
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 4.2977 | 9.4694 | 30.1118 | 12.7836 | 9.3272 | 9.4694 | 9.4256 | 12.706 | Offer with ENW, due to be signed 22/01/2025
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 10.9837 | 16.2088 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | N/A
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 8.5411 | 13.0411 | 27.8355 | 13.6992 | 9.8459 | 13.0411 | 9.8081 | 10.2615 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 15.8905 | 15.8905 | 15.2123 | 5.3923 | 3.9343 | 15.2123 | 3.8058 | 9.6649 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 9.2289 | 9.2289 | 23.2074 | 9.7365 | 7.104 | 9.2289 | 6.7909 | 5.3989 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 0.20802 | 9.208 | 17.9015 | 17.9015 | 17.3133 | 9.208 | 17.1739 | 8.8706 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 0 | 7.2156 | 1.188 | 0.85383 | 0 | 0.7451 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0 | 0 | 15.5363 | 8.6101 | 6.1883 | 0 | 4.4683 | 2.8737 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 7.037 | 11.174 | 11.2179 | 1.9575 | 1.4344 | 11.174 | 1.4344 | 8.2958 | Offer with ENW, due to be signed 27/2/2024
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.8954 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 8.4423 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Offer with ENW, due to be signed 27/2/2024
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 13.5303 | 34.5303 | 0.22922 | 0.037176 | 0.027125 | 0.22922 | 0.16545 | 1.3982 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.5233 | 17.5023 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 3.0596 | 5.5596 | 8.424 | 8.424 | 8.424 | 5.5596 | 8.424 | 5.5206 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 0 | 20.4258 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 13.1521 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW, due to be signed 27/2/2024
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 5.6307 | 10.2677 | 22.5101 | 3.6508 | 2.6637 | 10.2677 | 2.09 | 9.5109 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.5568 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 8.0361 | 13.2261 | 30.7725 | 16.359 | 11.936 | 13.2261 | 12.1148 | 12.9781 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 11.1463 | 24.4378 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 4.654 | 4.654 | 26.8249 | 4.3506 | 3.1743 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.427 | 8.747 | 11.2179 | 1.9575 | 1.4344 | 8.747 | 1.4344 | 8.4761 | Offer with ENW, due to be signed 27/2/2024
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 17.0193 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.9942 | 12.8942 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | N/A
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 5.4269 | 12.8269 | 31.5852 | 9.6474 | 7.0695 | 12.8269 | 7.3076 | 14.6753 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 4.4934 | 7.9934 | 22.4112 | 11.0957 | 8.0958 | 7.9934 | 8.0328 | 8.3048 | Offer with ENW, due to be signed 22/01/2025
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 7.144 | 11.781 | 31.3411 | 12.8171 | 9.2119 | 11.781 | 9.2691 | 12.9036 | Offer with ENW, due to be signed 22/01/2025
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.8479 | 2.8479 | 22.1947 | 15.2712 | 11.1423 | 2.8479 | 11.1639 | 2.7039 | Offer with ENW, due to be signed 27/2/2024
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 9.3464 | 16.0364 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 3.1435 | 8.1435 | 24.4081 | 9.2343 | 6.7376 | 8.1435 | 5.9831 | 2.9543 | PP submitted, offer due 12/12/2024
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.6031 | 13.9049 | 18.6656 | 18.6656 | 17.1151 | 13.9049 | 17.154 | 12.6129 | PP submitted, offer due 12/12/2024
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0 | 0 | 24.012 | 13.2834 | 9.547 | 0 | 5.1053 | 5.0492 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 4.757 | 10.757 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 9.12 | PP submitted, offer due 12/12/2024
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 0.93241 | 11.9324 | 18.6892 | 18.6892 | 16.2498 | 11.9324 | 7.0436 | 11.2916 | Offer signed 20/11/2024
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 5.7715 | 10.4085 | 26.0405 | 6.3986 | 4.6686 | 10.4085 | 2.9125 | 3.9899 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0 | 0 | 8.4614 | 1.9575 | 1.4344 | 0 | 1.5151 | 3.7068 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6258 | 19.3058 | 27.6988 | 10.7475 | 7.8417 | 19.3058 | 7.0436 | 19.3058 | Offer signed 20/11/2024
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 4.1479 | 7.6479 | 11.2179 | 1.9575 | 1.4344 | 7.6479 | 1.4344 | 7.8631 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 6.7153 | 7 | 1.9575 | 1.4344 | 6.7153 | 1.4344 | 4.7605 | Offer with ENW, due to be signed 27/2/2024
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 2.5795 | 18.1909 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 20/11/2024
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.1536 | 15.5785 | 43.3786 | 8.5607 | 6.2462 | 15.5785 | 1.845 | 13.1837 | Offer signed 20/11/2024
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.4823 | 4.8516 | 4.8516 | 4.8516 | 1.4823 | 4.8516 | 1.4303 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.3635 | 7.0005 | 23.0632 | 4.6267 | 3.3758 | 7.0005 | 2.296 | 3.1319 | N/A
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.2053 | 8.5053 | 11.2179 | 1.9575 | 1.4344 | 8.5053 | 1.4344 | 8.1583 | Offer with ENW, due to be signed 27/2/2024
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.0804 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 2.415 | 7.052 | 32.4077 | 6.9019 | 4.9605 | 7.052 | 0.088852 | 0 | Offer with ENW, due to be signed 27/2/2024
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 1.5693 | 13.5703 | 11.5154 | 8.4384 | 1.5693 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 9.939 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW, due to be signed 27/2/2024
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 1.548 | 9.028 | 32.4628 | 15.2339 | 10.9489 | 9.028 | 11.6712 | 8.928 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 4.976 | 15.7382 | 29.9539 | 12.5489 | 9.156 | 15.7382 | 9.1618 | 11.3246 | PP submitted, offer due 12/12/2024
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.3663 | 15.0033 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 5.9174 | 10.5544 | 11.2179 | 1.9575 | 1.4344 | 10.5544 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DICKINSON ST | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 4.976 | 11.4696 | 36.7251 | 12.5091 | 9.127 | 11.4696 | 9.5067 | 5.4068 | PP submitted, offer due 12/12/2024
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.3769 | 13.0139 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 11.2179 | PP submitted, offer due 12/12/2024
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 0.72949 | 0.72949 | 11.2179 | 1.9575 | 1.4344 | 0.72949 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.492 | 15.152 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 6.9119 | 11.5489 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.4097 | Offer signed 27/08/2024
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.0255 | 14.6625 | 22.7944 | 3.6969 | 2.6974 | 14.6625 | 2.6715 | 15.6217 | Offer signed 27/08/2024
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 4.0871 | 10.5871 | 11.2179 | 1.9575 | 1.4344 | 10.5871 | 1.4344 | 7.2779 | Offer with ENW, due to be signed 27/2/2024
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 20.0956 | 21.4956 | 10.7016 | 1.7619 | 1.2663 | 10.7016 | 0.99981 | 8.4492 | N/A
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 10.9278 | 15.5648 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 27/08/2024
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0.065726 | 2.8786 | 2.8786 | 2.8786 | 0.065726 | 2.8786 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 2.5874 | 5.0874 | 21.2377 | 16.8583 | 12.1164 | 5.0874 | 12.6319 | 4.995 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.2201 | 14.2201 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 0 | 6.1385 | 20.5513 | 3.5861 | 2.6279 | 6.1385 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 4.654 | 4.654 | 28.9569 | 8.5584 | 6.2715 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 6.5382 | 11.1752 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 11.2006 | PP submitted, offer due 12/12/2024
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 9.6808 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW, due to be signed 27/2/2024
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 0 | 14.9243 | 19.0252 | 3.5861 | 2.6279 | 14.9243 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 1.2618 | 14.0312 | 30.4491 | 15.4638 | 11.1142 | 14.0312 | 11.2192 | 5.6473 | Offer signed 27/08/2024
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 4.8583 | 11.0501 | 11.0501 | 11.0501 | 4.8583 | 11.0501 | 4.4257 | Offer signed 20/11/2024
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 12.8266 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 2.3169 | 8.8169 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 12.1782 | 12.5347 | 30.4947 | 12.211 | 8.9095 | 12.5347 | 8.6697 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 0.7447 | 0.7447 | 14.6333 | 10.4188 | 7.6348 | 0.7447 | 9.0987 | 0.2593 | N/A
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.4591 | 11.9591 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 1.6778 | 6.3148 | 32.1414 | 12.3777 | 9.0311 | 6.3148 | 8.9257 | 9.6892 | Offer signed 27/08/2024
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0 | 0 | 7.5611 | 7.5611 | 7.5611 | 0 | 7.4769 | 2.881 | PP submitted, offer due 16/01/2025
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 6.2572 | 18.2072 | 9.3746 | 1.5435 | 1.1093 | 9.3746 | 1.4212 | 12.0107 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.3598 | 12.9968 | 30.2846 | 5.2846 | 3.8725 | 12.9968 | 5.4751 | 12.055 | Offer signed 27/08/2024
GOLBORNE | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 0.21563 | 5.7156 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 4.6141 | 9.2511 | 29.9812 | 10.0377 | 7.2143 | 9.2511 | 7.0494 | 5.6473 | Offer signed 27/08/2024
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.2872 | 14.3872 | 24.7332 | 6.3982 | 4.6683 | 14.3872 | 5.885 | 14.3872 | Offer signed 20/11/2024
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.451 | 10.451 | 21.0097 | 21.0097 | 15.817 | 10.451 | 19.5311 | 10.7263 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 8.8093 | 16.9293 | 19.4454 | 3.3976 | 2.479 | 16.9293 | 1.1085 | 9.368 | Offer signed 20/11/2024
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 5.1819 | 9.8189 | 32.2668 | 15.6733 | 11.2647 | 9.8189 | 11.1508 | 10.8283 | N/A
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 0 | 3.2261 | 33.5043 | 8.7617 | 6.2972 | 3.2261 | 5.6166 | 0.45951 | Offer with ENW, due to be signed 22/01/2025
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0 | 3.4618 | 21.3921 | 9.13 | 6.6615 | 3.4618 | 4.1968 | 3.8848 | Offer signed 27/08/2024
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 1.9987 | 10.1549 | 32.3774 | 7.568 | 5.5218 | 10.1549 | 5.7981 | 10.2071 | Offer signed 27/08/2024
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 12.3312 | 16.8312 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 15.2042 | 19.885 | 55.5263 | 9.4166 | 6.8706 | 19.885 | 6.8407 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 0 | 13.3395 | 20.5513 | 3.5861 | 2.6279 | 13.3395 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 12.0416 | 16.7619 | 7.5869 | 1.2491 | 0.89777 | 7.5869 | 0.83754 | 7.0779 | Offer signed 27/08/2024
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 0 | 0 | 21.3624 | 10.3534 | 7.5541 | 0 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 7.2935 | 11.9305 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0 | 0 | 10.8975 | 10.8975 | 10.8975 | 0 | 5.1053 | 5.1053 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 5.6699 | 10.3069 | 31.6811 | 12.6537 | 9.2325 | 10.3069 | 9.5452 | 9.9239 | Offer signed 20/11/2024
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 11.024 | 15.664 | 30.4539 | 12.2843 | 8.963 | 15.664 | 9.1946 | 15.552 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 2.82 | 7.12 | 11.2179 | 1.9575 | 1.4344 | 7.12 | 1.4344 | 7.187 | Offer with ENW, due to be signed 27/2/2024
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 1.4258 | 4.9258 | 15.8004 | 4.8958 | 3.5187 | 4.9258 | 3.4214 | 6.4802 | Offer signed 27/08/2024
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.291 | 6.791 | 13.0026 | 13.0026 | 13.0026 | 6.791 | 13.0026 | 6.7952 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 11.2015 | 15.7015 | 30.5328 | 16.9131 | 12.1558 | 15.7015 | 12.0132 | 15.4515 | Offer with ENW, due to be signed 22/01/2025
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 6.8033 | 12.3033 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.1069 | 19.3269 | 3.5139 | 0.57854 | 0.41581 | 3.5139 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.1069 | 19.3269 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 4.0459 | 7.5459 | 24.7522 | 10.219 | 7.4561 | 7.5459 | 7.0425 | 7.7035 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 5.207 | 5.207 | 6.8624 | 1.9575 | 1.4344 | 5.207 | 1.4344 | 2.695 | Offer with ENW, due to be signed 27/2/2024
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.2144 | 17.4244 | 29.9937 | 9.0757 | 6.6219 | 17.4244 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 0 | 0 | 31.1274 | 9.5761 | 6.987 | 0 | 7.1221 | 0 | Offer with ENW, due to be signed 22/01/2025
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0 | 0 | 27.7432 | 4.4996 | 3.283 | 0 | 3.0681 | 0 | Offer with ENW, due to be signed 22/01/2025
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.45886 | 8.4589 | 13.2972 | 13.2972 | 13.2972 | 8.4589 | 13.2972 | 8.3367 | Offer signed 20/11/2024
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 12.9669 | 17.1039 | 25.8852 | 11.8132 | 8.4904 | 17.1039 | 9.101 | 17.1039 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.6561 | 14.2931 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 10.1531 | 14.7901 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 6.0399 | 7.1711 | 16.0172 | 2.5978 | 1.8954 | 7.1711 | 1.2885 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 4.9497 | 12.4497 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 3.0994 | 7.7364 | 21.3152 | 5.4084 | 3.8871 | 7.7364 | 3.7037 | 4.126 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 8.6482 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW, due to be signed 27/2/2024
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0.95096 | Offer with ENW, due to be signed 27/2/2024
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 2.7667 | 6.5025 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Offer with ENW, due to be signed 27/2/2024
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 4.654 | 4.654 | 26.6633 | 7.111 | 5.1884 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.819 | 10.956 | 11.2179 | 1.9575 | 1.4344 | 10.956 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 3.397 | 6.897 | 11.2179 | 1.9575 | 1.4344 | 6.897 | 1.4344 | 6.5258 | Offer with ENW, due to be signed 27/2/2024
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 5.5232 | 9.0232 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 0 | 0 | 21.6275 | 20.4617 | 14.9941 | 0 | 17.2503 | 13.3736 | PP submitted, offer due 16/01/2025
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.2795 | 10.9165 | 30.2846 | 5.2846 | 3.8725 | 10.9165 | 5.4751 | 11.4433 | Offer signed 27/08/2024
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.8125 | 17.1125 | 29.3612 | 13.5952 | 9.9194 | 17.1125 | 7.0436 | 17.6125 | Offer signed 20/11/2024
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 0 | 15.9252 | 20.5513 | 3.5861 | 2.6279 | 15.9252 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 9.0341 | 12.6981 | 12.6981 | 12.6981 | 9.0341 | 0 | 0 | PP submitted, offer due 16/01/2025
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 3.0981 | 7.2381 | 11.2179 | 1.9575 | 1.4344 | 7.2381 | 1.4344 | 4.4053 | N/A
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 7.0226 | 11.1596 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.3013 | 17.4383 | 29.8132 | 13.3488 | 9.7396 | 17.4383 | 7.0436 | 16.5205 | Offer signed 20/11/2024
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 6.4707 | 28.0218 | 9.4094 | 6.7628 | 6.4707 | 0 | 0 | PP submitted, offer due 16/01/2025
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 3.2127 | 5.7127 | 7 | 1.9575 | 1.4344 | 5.7127 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 12.5347 | 12.5347 | 45.8137 | 8.4279 | 6.0573 | 12.5347 | 1.6009 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.81619 | 2.3162 | 3.1954 | 3.1954 | 3.1954 | 2.3162 | 3.1954 | 2.3112 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 6.1741 | 13.7662 | 13.7662 | 13.7662 | 6.1741 | 0 | 0 | PP submitted, offer due 16/01/2025
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.2241 | 5.7241 | 3.4566 | 3.4566 | 3.4566 | 3.4566 | 2.8987 | 2.8987 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 0 | 0 | 19.5904 | 19.5904 | 14.9941 | 0 | 19.5904 | 10.2783 | PP submitted, offer due 16/01/2025
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 0 | 0 | 29.4281 | 20.4617 | 14.9941 | 0 | 18.6543 | 13.2545 | PP submitted, offer due 16/01/2025
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 3.9341 | 6.2841 | 19.9589 | 11.3858 | 8.1832 | 6.2841 | 8.0695 | 0 | Offer with ENW, due to be signed 27/2/2024
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 0 | 10.9081 | 31.9515 | 12.5496 | 9.1565 | 10.9081 | 9.0797 | 10.8837 | Offer signed 27/08/2024
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 4.211 | 31.367 | 6.9221 | 5.0506 | 4.211 | 4.9077 | 0 | PP submitted, offer due 12/12/2024
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 0 | 14.0221 | 24.478 | 9.5361 | 6.9578 | 14.0221 | 7.0795 | 15.6051 | Offer signed 27/08/2024
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 2.7658 | 4.654 | 33.1798 | 8.5584 | 6.2715 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 2.5795 | 15.0194 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 20/11/2024
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.3639 | 6.5025 | 19.6186 | 19.6186 | 19.6186 | 6.5025 | 19.6186 | 0 | Offer with ENW, due to be signed 27/2/2024
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 1.6861 | 5.1861 | 25.4427 | 13.7594 | 10.0392 | 5.1861 | 10.1941 | 6.1719 | Offer with ENW, due to be signed 22/01/2025
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 13.7639 | 21.549 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 4.4452 | 7 | 1.9575 | 1.4344 | 4.4452 | 1.4344 | 4.4466 | Offer with ENW, due to be signed 27/2/2024
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 0 | 0 | 16.5605 | 16.5605 | 14.9941 | 0 | 16.5605 | 4.0762 | PP submitted, offer due 16/01/2025
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 2.0518 | 5.5518 | 25.0991 | 9.8481 | 7.1854 | 5.5518 | 6.9929 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 10.3372 | 14.9742 | 31.2344 | 7.8116 | 5.6996 | 14.9742 | 5.7031 | 10.4658 | PP submitted, offer due 12/12/2024
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 0.72949 | 0.72949 | 11.2179 | 1.9575 | 1.4344 | 0.72949 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 2.6322 | 6.7692 | 27.2475 | 5.3428 | 3.8983 | 6.7692 | 2.8907 | 9.1882 | Offer with ENW, due to be signed 22/01/2025
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 0.96728 | 6.9673 | 35.3525 | 5.8205 | 4.1833 | 6.9673 | 0.088852 | 0 | Offer with ENW, due to be signed 27/2/2024
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 0 | 16.0134 | 20.5513 | 3.5861 | 2.6279 | 16.0134 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 15.0206 | 19.6576 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.6576 | N/A
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 0.72762 | 30.0909 | 10.1955 | 7.4389 | 0.72762 | 7.4513 | 1.5496 | Offer with ENW, due to be signed 22/01/2025
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0.050606 | 0.050606 | 7.1061 | 7.1061 | 7.1061 | 0.050606 | 7.1061 | 0 | Offer with ENW, due to be signed 22/01/2025
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 10.4104 | 15.0104 | 24.6386 | 8.3795 | 6.1139 | 15.0104 | 6.5522 | 14.5624 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 8.8458 | 17.5694 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.358 | 7.1573 | 7.1573 | 7.1573 | 3.358 | 0 | 0 | PP submitted, offer due 16/01/2025
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 0 | 0 | 21.3624 | 12.8802 | 9.3977 | 0 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 4.654 | 4.654 | 26.5902 | 4.3779 | 3.1465 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 8.8016 | 11.6014 | 18.7067 | 18.7067 | 17.7936 | 11.6014 | 18.0835 | 11.4916 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 10.2974 | 14.9374 | 30.1883 | 10.3446 | 7.5477 | 14.9374 | 7.4802 | 14.0754 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 7.494 | 14.5672 | 2.3984 | 1.7238 | 7.494 | 0 | 0 | PP submitted, offer due 16/01/2025
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 6.6836 | 10.1836 | 11.2179 | 1.9575 | 1.4344 | 10.1836 | 1.4344 | 0 | Offer signed 27/08/2024
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 3.8631 | 7.3631 | 11.2179 | 1.9575 | 1.4344 | 7.3631 | 1.4344 | 5.0297 | N/A
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 1.9596 | 5.4596 | 11.2179 | 1.9575 | 1.4344 | 5.4596 | 1.4344 | 8.9507 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 8.3041 | 12.1041 | 0.65256 | 0.24769 | 0.20239 | 0.65256 | 0.31765 | 2.6844 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 1.7166 | 5.2166 | 23.7167 | 9.1683 | 6.6895 | 5.2166 | 5.8695 | 0 | PP submitted, offer due 12/12/2024
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 4.1574 | 7 | 1.9575 | 1.4344 | 4.1574 | 1.4344 | 3.7702 | Offer with ENW, due to be signed 27/2/2024
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 15.1124 | 21.6597 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.3845 | 6.6985 | 27.9116 | 12.7356 | 9.1533 | 6.6985 | 9.1199 | 4.5253 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.8462 | 31.5971 | 10.291 | 7.5086 | 2.8462 | 7.5673 | 1.6732 | Offer with ENW, due to be signed 22/01/2025
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 9.3376 | 13.9746 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 10.6685 | 15.3054 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.7054 | N/A
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.588 | 14.208 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 27/2/2024
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 1.4208 | 5.5608 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 20/11/2024
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 4.654 | 4.654 | 31.0839 | 8.5584 | 6.2715 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 0 | 3.8322 | 3.8322 | 3.8322 | 0 | 3.8322 | 2.0546 | PP submitted, offer due 16/01/2025
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0 | 0 | 15.0523 | 15.0523 | 14.9941 | 0 | 15.0523 | 7.0631 | PP submitted, offer due 16/01/2025
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.7563 | 15.5143 | 8.0566 | 5.2846 | 3.8725 | 8.0566 | 1.511 | 1.511 | Offer signed 27/08/2024
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 1.9905 | 1.9905 | 12.0025 | 8.5584 | 6.2715 | 1.9905 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 8.7634 | 12.9004 | 28.3704 | 11.1433 | 8.0089 | 12.9004 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 28.4951 | 4.6915 | 3.3719 | 0 | 3.841 | 8.6565 | PP submitted, offer due 16/01/2025
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 16.5236 | 16.5236 | 14.9941 | 0 | 14.4183 | 10.2752 | PP submitted, offer due 16/01/2025
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.3747 | 22.8902 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 10.47 | 15.107 | 8.1008 | 1.3337 | 0.95858 | 8.1008 | 0.56343 | 4.7615 | Offer with ENW, due to be signed 22/01/2025
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 7.508 | 11.008 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 9.31 | PP submitted, offer due 12/12/2024
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 2.9549 | 7.8949 | 11.2179 | 1.9575 | 1.4344 | 7.8949 | 1.4344 | 10.0382 | N/A
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 0 | 0 | 30.5974 | 12.4652 | 9.0949 | 0 | 9.1327 | 0 | Offer with ENW, due to be signed 22/01/2025
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 2.3632 | 5.8632 | 11.2179 | 1.9575 | 1.4344 | 5.8632 | 1.4344 | 5.886 | Offer signed 27/08/2024
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 8.7868 | 13.4238 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 10.8461 | 18.7537 | 6.7033 | 1.1036 | 0.79321 | 6.7033 | 0.84345 | 7.1279 | Offer signed 20/11/2024
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0 | 8.8523 | 19.6031 | 19.6031 | 19.6031 | 8.8523 | 19.6031 | 8.983 | Offer signed 20/11/2024
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 14.6928 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 7.9823 | 12.1193 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 1.4954 | 10.4954 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 20/11/2024
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 4.976 | 16.5633 | 29.5281 | 8.4739 | 6.1828 | 16.5633 | 6.0414 | 15.0117 | PP submitted, offer due 12/12/2024
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 8.503 | 21.7465 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 7.7571 | 11.5571 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 0 | 0 | 31.2648 | 9.1525 | 6.6779 | 0 | 6.7371 | 0 | Offer with ENW, due to be signed 22/01/2025
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 9.0759 | 11.0559 | 11.2179 | 1.9575 | 1.4344 | 11.0559 | 1.4344 | 6.9765 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 6.697 | 10.197 | 23.6228 | 13.2243 | 9.5046 | 10.197 | 9.4181 | 10.8112 | Offer with ENW, due to be signed 22/01/2025
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 11.2011 | 15.7011 | 26.8965 | 10.4188 | 7.6348 | 15.7011 | 9.0987 | 15.8281 | N/A
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 0.72949 | 0.72949 | 2.6918 | 0.43658 | 0.31854 | 0.72949 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 11.301 | 15.938 | 30.2268 | 11.7941 | 8.6053 | 15.938 | 8.77 | 17.138 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 5.5826 | 10.2196 | 32.1779 | 7.956 | 5.8049 | 10.2196 | 5.8553 | 6.3816 | Offer with ENW, due to be signed 27/2/2024
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 5.0473 | 12.6073 | 30.2531 | 12.325 | 8.9927 | 12.6073 | 8.8549 | 17.2513 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.2872 | 14.3872 | 24.7332 | 11.0855 | 8.0883 | 14.3872 | 9.5083 | 14.3872 | Offer signed 20/11/2024
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 7.051 | 9.0713 | 11.2179 | 1.9575 | 1.4344 | 9.0713 | 1.4344 | 0 | Offer signed 27/08/2024
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 8.7161 | 9.1161 | 43.9949 | 11.7821 | 8.468 | 9.1161 | 8.7443 | 5.7413 | Offer with ENW, due to be signed 27/2/2024
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 5.4637 | 18.1637 | 34.9192 | 12.5755 | 9.1754 | 18.1637 | 8.8192 | 17.3639 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.6415 | 15.2785 | 30.169 | 15.9266 | 11.6205 | 15.2785 | 11.7382 | 14.2835 | Offer signed 20/11/2024
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 0 | 0 | 30.3545 | 9.8345 | 7.1756 | 0 | 7.0914 | 0 | Offer with ENW, due to be signed 22/01/2025
RIBBLESDALE T13 & RIBBLESDALE T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 1.934 | 4.684 | 22.1282 | 15.8208 | 11.3707 | 4.684 | 11.8923 | 1.683 | Offer signed 20/11/2024
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 0.72949 | 0.72949 | 11.2179 | 1.9575 | 1.4344 | 0.72949 | 1.4344 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 9.003 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW, due to be signed 27/2/2024
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 10.2641 | 8.8484 | 1.4568 | 1.047 | 8.8484 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 11.807 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 17.4155 | 30.4155 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 0 | 14.7322 | 20.5513 | 3.5861 | 2.6279 | 14.7322 | 0 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 0 | 0 | 24.0007 | 10.8395 | 7.7906 | 0 | 7.5834 | 0 | Offer with ENW, due to be signed 22/01/2025
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 0 | 3.109 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 10.1919 | 14.8289 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 11.4457 | 16.0857 | 31.0489 | 8.4625 | 6.1745 | 16.0857 | 6.5677 | 14.7385 | N/A
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 1.5401 | 1.5401 | 12.01 | 12.01 | 12.01 | 1.5401 | 12.01 | 1.3941 | N/A
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 16.67 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 11.68 | 16.18 | 30.3 | 17.8324 | 12.8165 | 16.18
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 8.0044 | 12.5044 | 30.2683 | 9.6474 | 7.0695 | 12.5044 | 7.2924 | 14.3266 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.1832 | 3.6832 | 6.4667 | 1.9575 | 1.4344 | 3.6832 | 1.4344 | 3.6656 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0 | 0.36018 | 1.9438 | 1.9438 | 1.4344 | 0.36018 | 1.4344 | 1.1732 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 10.2776 | 19.5532 | 19.5532 | 19.3279 | 10.2776 | 0 | 0 | PP submitted, offer due 16/01/2025
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0 | 0 | 4.9054 | 4.9054 | 4.9054 | 0 | 4.9054 | 1.1883 | PP submitted, offer due 16/01/2025
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.45821 | 7.9582 | 13.3716 | 13.3716 | 13.3716 | 7.9582 | 13.3716 | 7.6618 | Offer signed 20/11/2024
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.0585 | 7.4085 | 32.0548 | 26.4246 | 18.9919 | 7.4085 | 18.9995 | 5.2353 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 4.417 | 9.917 | 32.1479 | 10.8122 | 7.8889 | 9.917 | 8.0106 | 5.397 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 0 | 0 | 12.2325 | 12.2325 | 12.2325 | 0 | 12.2325 | 7.0318 | PP submitted, offer due 16/01/2025
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 9.6466 | 14.2836 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.154 | 23.7448 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 16.1247 | 38.4633 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 4.1048 | 8.7418 | 11.2179 | 1.9065 | 1.3702 | 8.7418 | 1.3976 | 7.809 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 0 | 0 | 30.438 | 20.4617 | 14.9941 | 0 | 17.7881 | 13.3736 | PP submitted, offer due 16/01/2025
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 5.9979 | 7.9979 | 16.7034 | 16.6499 | 11.9666 | 7.9979 | 12.7115 | 7.3459 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 6.865 | 11.502 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 27/08/2024
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 7.7459 | 7.7459 | 11.2179 | 1.9575 | 1.4344 | 7.7459 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.4307 | 18.053 | 29.4531 | 11.4584 | 8.2354 | 18.053 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.979 | 7.116 | 11.2179 | 1.9575 | 1.4344 | 7.116 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 5.2005 | 5.2005 | 11.2179 | 1.9575 | 1.4344 | 5.2005 | 1.4344 | 5.2215 | Offer with ENW, due to be signed 27/2/2024
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 25.7295 | 32.7295 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 6.472 | 9.972 | 23.6188 | 13.3814 | 9.7634 | 9.972 | 4.1691 | 9.6296 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 2.5795 | 18.7784 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 20/11/2024
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 5.7961 | 10.3961 | 16.6857 | 2.7062 | 1.9745 | 10.3961 | 2.1114 | 6.2955 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 9.1032 | 12.6032 | 23.0658 | 9.7444 | 7.1098 | 12.6032 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 9.6203 | 14.2573 | 29.2752 | 10.1042 | 7.3723 | 14.2573 | 7.7148 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 7.1664 | 10.6664 | 11.2179 | 1.9575 | 1.4344 | 10.6664 | 1.4344 | 10.0664 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 13.7705 | 18.053 | 30.1228 | 12.8233 | 9.3562 | 18.053 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.1817 | 10.6817 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0 | 0 | 20.7493 | 7.5777 | 5.4463 | 0 | 1.9914 | 1.9914 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 12.7565 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 5.2912 | 9.4282 | 20.9842 | 3.4093 | 2.4875 | 9.4282 | 2.4384 | 6.5078 | Offer signed 20/11/2024
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 7.9793 | 14.9793 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 9.7731 | 26.7731 | 25.8443 | 4.2551 | 3.0582 | 25.8443 | 2.782 | 23.5098 | Offer signed 20/11/2024
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.6986 | 18.1986 | 30.2092 | 14.9211 | 10.7241 | 18.1986 | 10.853 | 18.1986 | Offer with ENW, due to be signed 27/2/2024
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 7.1554 | 11.7924 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 9.276 | 13.413 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0 | 0 | 20.8292 | 7.4375 | 5.3455 | 0 | 0.31765 | 2.6844 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 4.6961 | 15.3961 | 29.77 | 10.0632 | 7.3424 | 15.3961 | 7.3789 | 14.5981 | Offer with ENW, due to be signed 27/2/2024
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 17.9353 | 26.4 | 5.768 | 1.9575 | 1.4344 | 5.768
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 8.6442 | 11.7812 | 11.2179 | 1.932 | 1.3886 | 11.2179 | 0.31765 | 2.6844 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 4.654 | 4.654 | 33.4932 | 8.5584 | 6.2715 | 4.654 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 7.3565 | 14.3565 | 22.3705 | 7.7115 | 5.6265 | 14.3565 | 5.7122 | 14.3365 | PP submitted, offer due 12/12/2024
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 6.2399 | 11.4899 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | N/A
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 20.0999 | 20.0999 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 21.7432 | 0 | 0 | 0 | 0 | 0 | 0 | Offer with ENW, due to be signed 27/2/2024
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 7.3748 | 11.5118 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 5.727 | 8.727 | 16.3552 | 10.2012 | 7.3318 | 8.727 | 7.6223 | 7.75 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 1.9788 | 6.6158 | 11.2179 | 1.9575 | 1.4344 | 6.6158 | 1.4344 | 9.7198 | Offer with ENW, due to be signed 27/2/2024
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 0 | 6.8611 | 22.0084 | 11.0663 | 7.9535 | 6.8611 | 8.1328 | 6.6945 | Offer signed 27/08/2024
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 11.1241 | 15.7611 | 28.9446 | 7.9227 | 5.7806 | 15.7611 | 5.7691 | 14.4783 | PP submitted, offer due 12/12/2024
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 5.1043 | 25.5112 | 8.2657 | 6.0308 | 5.1043 | 4.6312 | 4.9475 | Offer with ENW, due to be signed 22/01/2025
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.4371 | 10.9371 | 11.2179 | 1.9575 | 1.4344 | 10.9371 | 1.4344 | 10.9371 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 5.8835 | 10.5205 | 31.4551 | 7.972 | 5.8166 | 10.5205 | 5.5739 | 0 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 0 | 0 | 21.3624 | 12.6444 | 9.2257 | 0 | 0 | 0 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 14.6569 | 19.2939 | 29.365 | 12.5831 | 9.181 | 19.2939 | 9.344 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 2.2895 | 2.2895 | 28.4979 | 11.225 | 8.0676 | 2.2895 | 1.3561 | 10.6051 | Offer signed 27/08/2024
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 11.5011 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer with ENW, due to be signed 27/2/2024
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 13.7613 | 18.3983 | 30.177 | 12.1986 | 8.9005 | 18.3983 | 8.8768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 12.7289 | 17.3659 | 30.2639 | 13.4467 | 9.8111 | 17.3659 | 10.1945 | 7.7239 | Offer signed 20/11/2024
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7897 | 10.7897 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 8.6933 | PP submitted, offer due 12/12/2024
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0 | 4.5846 | 11.4082 | 1.8783 | 1.35 | 4.5846 | 0.088852 | 0 | Offer with ENW, due to be signed 27/2/2024
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 5.6143 | 8.7506 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 8.5757 | 13.2127 | 28.3048 | 7.9578 | 5.7194 | 13.2127 | 5.5392 | 11.0853 | Offer signed 20/11/2024
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 2.5842 | 11.7212 | 8.816 | 1.9575 | 1.4344 | 8.816 | 1.4344 | 10.576 | PP submitted, offer due 12/12/2024
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 5.5937 | 23.0587 | 19.4594 | 13.9858 | 5.5937 | 0 | 0 | PP submitted, offer due 16/01/2025
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.5236 | 9.0236 | 23.9575 | 14.5121 | 10.4302 | 9.0236 | 10.3146 | 9.0214 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 4.6744 | 6.1744 | 10.5081 | 4.5903 | 3.3492 | 6.1744 | 3.1391 | 5.9064 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0 | 2.1865 | 7 | 1.9575 | 1.4344 | 2.1865 | 1.4344 | 0.21045 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 8.5302 | 13.1672 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 1.1806 | 4.6806 | 25.3471 | 12.5884 | 9.1849 | 4.6806 | 9.2635 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 6.9548 | 11.0918 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 4.8885 | 8.3885 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | PP submitted, offer due 12/12/2024
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 10.2776 | 30.4268 | 20.4819 | 14.7208 | 10.2776 | 0 | 0 | PP submitted, offer due 16/01/2025
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 5.4547 | 8.9547 | 18.0363 | 6.6753 | 4.8705 | 8.9547 | 2.1791 | 7.5047 | Offer with ENW, due to be signed 22/01/2025
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.7832 | 6.2832 | 8.816 | 1.9575 | 1.4344 | 6.2832 | 1.4344 | 6.0832 | PP submitted, offer due 12/12/2024
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 7.7459 | 7.7459 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | PP submitted, awaiting Clock Start date
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.6856 | 9.1856 | 24.1055 | 14.309 | 10.4402 | 9.1856 | 10.5673 | 8.8316 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0 | 0 | 30.1487 | 13.9978 | 10.0605 | 0 | 5.1053 | 5.1053 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 2.7595 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 1.0021 | 4.5021 | 5.768 | 1.9575 | 1.4344 | 4.5021 | 1.4344 | 0.86929 | PP submitted, offer due 12/12/2024
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 0 | 0 | 10.7344 | 1.7673 | 1.2702 | 0 | 1.0921 | 0 | Offer with ENW, due to be signed 22/01/2025
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 10.6754 | 14.6754 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 27/2/2024
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 8.8855 | 13.5225 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 27/2/2024
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 1.9987 | 11.9477 | 26.1692 | 10.8708 | 7.9316 | 11.9477 | 7.7377 | 8.7753 | Offer signed 27/08/2024
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0 | 0 | 30.4446 | 15.21 | 10.9317 | 0 | 5.1053 | 5.1053 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 6.5082 | 12.8478 | 12.8478 | 12.8478 | 6.5082 | 0 | 0 | PP submitted, offer due 16/01/2025

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 52.3544 | 70.3544 | 142.4601 | 46.9133 | 70.3544 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 17.361 | 29.361 | 91.3244 | 27.3279 | 29.361 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 53.6288 | 71.6288 | 149.5819 | 49.1274 | 71.6288 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | N/A
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 6.5025 | 6.5025 | 119.9397 | 27.7425 | 6.5025 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
BARROW | 33 | HARKER | 319709 | 470489 | 37.1162 | 45.1162 | 52.5902 | 9.5407 | 45.1162 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
BARTON | 33 | CARRINGTON | 376758 | 397174 | 52.4043 | 74.3995 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | N/A
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 12.5347 | 12.5347 | 54.6806 | 22.858 | 12.5347 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 36.5166 | 36.5166 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 38.1241 | 38.1241 | 68.8709 | 38.9615 | 38.1241 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 40.1977 | 41.0377 | 119.4893 | 35.4288 | 41.0377 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 4.976 | 54.4198 | 152.6811 | 48.1323 | 54.4198 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | PP submitted, offer due 12/12/2024
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 18.2531 | 30.9453 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 63.388 | 63.388 | 80.2594 | 29.0637 | 63.388 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
BURY | 33 | KEARSLEY | 380272 | 411184 | 26.2702 | 26.2702 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 2.2895 | 2.2895 | 63.2157 | 11.9066 | 2.2895 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Offer signed 27/08/2024
CARLISLE | 33 | HARKER | 338655 | 556583 | 19.9369 | 41.1369 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 11.7485 | 32.7485 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | N/A
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 46.542 | 46.542 | 103.112 | 37.4783 | 46.542 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 4.654 | 4.654 | 46.6537 | 8.4637 | 4.654 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 36.1403 | 36.1403 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Offer signed 27/08/2024
EGREMONT | 33 | HARKER | 301070 | 513074 | 51.09 | 51.09 | 33.6452 | 33.6452 | 33.6452 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 21.7432 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
GOLBORNE | 33 | BOLD | 360607 | 397690 | 33.3927 | 51.3927 | 62.7732 | 11.3881 | 51.3927 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 19.885 | 19.885 | 71.389 | 15.7509 | 19.885 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 37.4173 | 55.4173 | 137.0032 | 36.7376 | 55.4173 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 30.2812 | 92.2812 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Offer signed 27/08/2024
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 38.0422 | 56.0422 | 74.3197 | 21.9301 | 56.0422 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | Offer signed 20/11/2024
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 32.1548 | 32.1548 | 28.8073 | 5.2261 | 28.8073 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Offer signed 27/08/2024
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 29.4904 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 10.2776 | 108.9064 | 29.4951 | 10.2776 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | PP submitted, offer due 16/01/2025
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 12.6152 | 27.5792 | 124.2442 | 32.9735 | 27.5792 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 3.8644 | 21.8644 | 149.1089 | 38.9987 | 21.8644 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 0 | 46.0228 | 19.5488 | 3.5465 | 19.5488 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 18.053 | 18.053 | 42.8677 | 40.6628 | 18.053 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 7.7459 | 7.7459 | 10.6707 | 1.9358 | 7.7459 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | PP submitted, awaiting Clock Start date
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 17.9353 | 43.1353 | 5.5462 | 1.9358 | 5.5462 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | PP submitted, offer due 12/12/2024
NELSON | 33 | PADIHAM | 385989 | 438643 | 2.5795 | 23.9923 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | Offer signed 20/11/2024
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 20.9091 | 20.9091 | 53.1931 | 53.1931 | 20.9091 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Offer signed 27/08/2024
ORRELL | 33 | KIRKBY | 352784 | 404565 | 0 | 20.644 | 104.8901 | 43.9965 | 20.644 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Offer signed 27/08/2024
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 10.8461 | 44.7079 | 139.7763 | 31.5257 | 44.7079 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | Offer signed 20/11/2024
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 0 | 0 | 21.3624 | 21.3624 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
PENRITH | 33 | HUTTON | 349996 | 530398 | 0 | 0 | 33.5447 | 20.2354 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | PP submitted, offer due 16/01/2025
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 0.72949 | 0.72949 | 10.6707 | 1.9358 | 0.72949 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 42.6793 | 60.9756 | 145.8409 | 32.177 | 60.9756 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 76.3639 | 112.3639 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 46.4275 | 58.4275 | 94.6521 | 40.5681 | 58.4275 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 42.092 | 53.6903 | 106.8182 | 53.4018 | 53.6903 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | Offer signed 20/11/2024
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 17.421 | 94.3996 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 33 | CARRINGTON | 378726 | 392892 | 24.5357 | 24.5357 | 78.4545 | 48.3177 | 24.5357 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | N/A
SANDGATE | 33 | HARKER | 321492 | 468870 | 37.1162 | 45.1162 | 114.6293 | 20.7956 | 45.1162 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SHAP | 33 | HUTTON | 356910 | 513357 | 0 | 0 | 33.5447 | 33.5447 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | PP submitted, offer due 16/01/2025
SIDDICK | 33 | HARKER | 300332 | 530823 | 39.138 | 83.238 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 21.7465 | 21.7465 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
STAINBURN | 33 | HARKER | 302535 | 529330 | 39.138 | 83.238 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 13.3312 | 59.958 | 131.4503 | 33.6323 | 59.958 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | PP submitted, offer due 12/12/2024
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 11.1463 | 36.6463 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Offer signed 27/08/2024
THORNTON | 33 | STANAH | 334559 | 443368 | 12.1341 | 24.1341 | 26.8965 | 10.3035 | 24.1341 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | N/A
ULVERSTON | 33 | HARKER | 327495 | 477808 | 31.0038 | 31.0038 | 35.2954 | 21.346 | 31.0038 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 0 | 0 | 88.1369 | 16.2518 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 16.2001 | 52.7001 | 8.4769 | 1.9358 | 8.4769 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | PP submitted, offer due 12/12/2024
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 19.3161 | 19.3161 | 88.0127 | 24.9712 | 19.3161 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Offer with ENW, due to be signed 27/2/2024
WIGAN | 33 | KIRKBY | 358343 | 404626 | 1.9987 | 40.9987 | 87.9264 | 35.3832 | 40.9987 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Offer signed 27/08/2024
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0 | 0 | 47.1158 | 21.3332 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025

## 6)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | 0 | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 282 | 0 | C | 0 | 426.2 | 3 | Offer with ENW, due to be signed 22/01/2025
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 0 | 0 | B | 0 | 199 | 5.13 | N/A
HARKER | HARKER | 765.4 | 71 | 0 | 1036.6 | 0 | C | 324.8 | 1873 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025
HUTTON | HUTTON | 47.9 | 53 | 0 | 151 | 0 | D | 129.9 | 251.9 | 0 | PP submitted, offer due 16/01/2025
HEYSHAM | HEYSHAM | 292.6 | 0 | 109 | 21.5 | 0 | C | 199.8 | 423.1 | 0 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025
KEARSLEY | KEARSLEY | 57.9 | 264.7 | 11 | 35 | 0 | C | 0 | 368.6 | 3 | Offer with ENW, due to be signed 27/2/2024
KIRKBY | KIRKBY | 6 | 146.4 | 0 | 80.9 | 0 | D | 0 | 233.3 | 3 | Offer signed 27/08/2024
MACCLESFIELD | MACCLESFIELD | 27.9 | 30 | 0 | 0 | 0 | C | 7.5 | 57.9 | 2.57 | PP submitted, awaiting Clock Start date
PADIHAM | PADIHAM | 35.5 | 135.1 | 219.9 | 164.9 | 0 | D | 0 | 829.2 | 0.837 | Offer signed 20/11/2024
PENWORTHAM | PENWORTHAM | 187.9 | 601.1 | 67.6 | 253.2 | 0 | D | 153.6 | 1109.8 | 9.21 | Offer with ENW, due to be signed 23/01/2025,another parrallel submission, offer due 17/01/2025
ROCHDALE | ROCHDALE | 204.1 | 179.1 | 35 | 221.3 | 0 | C | 85 | 639.5 | 3 | Offers signed 26/09/2024. PP submitted, offer due 13/02/2025
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 420.8 | 0 | C | 169.9 | 524.3 | 3 | PP submitted, offer due 12/12/2024
STALYBRIDGE | STALYBRIDGE | 58.3 | 236.8 | 0 | 50 | 20 | C | 0 | 365.1 | 0.591 | Offer signed 27/08/2024
STANAH | STANAH | 195.9 | 142 | 0 | 0 | 0 | B | 0 | 349.4 | 3.01 | N/A
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 51.9 | 0 | D | 0 | 161 | 3 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WHITEGATE | WHITEGATE | 32 | 219.8 | 0 | 128.2 | 0 | C | 0 | 380 | 3.09 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application. D. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New GSPs have now been trigged by the latest Project progression return by ESO.