## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2025-02-11
This version is 539 days old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2024-12-08
This version is 604 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 0 | 11.6548 | 21.1 | 3.6819 | 2.698 | 11.6548 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 9.3284 | 16.0184 | 5.768 | 1.9575 | 1.4344 | 5.768 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0 | 3.3047 | 3.3047 | 3.3047 | 0 | 3.2626 | 1.1073 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 10.0598 | 29.6287 | 25.0296 | 17.9892 | 10.0598 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 5.1424 | 9.2794 | 32.3302 | 6.2179 | 4.5368 | 9.2794 | 4.8939 | 0.33304 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 6.1753 | 10.9253 | 19.2839 | 19.2839 | 15.5997 | 10.9253 | 15.7536 | 7.6053 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 3.4652 | 8.9652 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 5.0789 | 8.0789 | 21.7548 | 9.4452 | 6.8914 | 8.0789 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0.47844 | 5.4784 | 11.2179 | 1.9575 | 1.4344 | 5.4784 | 1.4344 | 0 | Offer signed 27/08/2024
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 10.0598 | 18.3845 | 18.3845 | 18.3845 | 10.0598 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 0.94597 | 26.2485 | 8.5874 | 6.2656 | 0.94597 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.9452 | 1.9452 | 5.57 | 1.9575 | 1.4344 | 1.9452 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 9.5983 | 13.7383 | 28.8941 | 8.6399 | 6.3039 | 13.7383 | 6.5315 | 13.4847 | PP submitted, awaiting Clock Start date
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 4.9687 | 9.1057 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9141 | 11.6641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 2.0975 | 2.0975 | 31.4391 | 10.1584 | 7.4118 | 2.0975 | 1.3561 | 10.6051 | Offer signed 27/08/2024
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 1.548 | 8.528 | 11.7207 | 6.6047 | 4.7469 | 8.528 | 6.4697 | 8.428 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92953 | 1.6295 | 3.9789 | 3.9789 | 3.9789 | 1.6295 | 3.9789 | 1.6295 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 3.4698 | 5.4698 | 7 | 1.9575 | 1.4344 | 5.4698 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 6.3779 | 8.6289 | 29.5385 | 4.8633 | 3.4953 | 8.6289 | 3.7461 | 0 | Offer signed 24/12/2024
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 5.3292 | 8.8292 | 22.71 | 13.163 | 9.6041 | 8.8292 | 9.6723 | 7.1892 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 0.66949 | 0.66949 | 11.2179 | 1.9575 | 1.4344 | 0.66949 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 3.6678 | 8.3048 | 30.0013 | 9.7582 | 7.0134 | 8.3048 | 7.6584 | 8.6278 | PP submitted, awaiting Clock Start date
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 4.7593 | 8.8963 | 11.2179 | 1.9575 | 1.4344 | 8.8963 | 1.4344 | 10.2623 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 3.1045 | 11.2179 | 1.9575 | 1.4344 | 3.1045 | 1.4344 | 9.8525 | Offer signed 24/12/2024
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.8644 | 18.3644 | 21.1384 | 9.9788 | 7.172 | 18.3644 | 8.0292 | 18.3194 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 3.9941 | 10.2441 | 11.2179 | 1.9575 | 1.4344 | 10.2441 | 1.4344 | 10.2441 | PP submitted, awaiting Clock Start date
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 4.9221 | 8.6289 | 28.5003 | 10.1159 | 7.2705 | 8.6289 | 7.2768 | 0 | Offer signed 24/12/2024
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.1244 | 10.6244 | 23.1258 | 11.5609 | 8.4352 | 10.6244 | 9.5768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.8921 | 9.8921 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 9.8921 | Offer with ENW, due to be signed 11/03/2025
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 5.2812 | 7.259 | 7.259 | 7.259 | 5.2812 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 4.9191 | 9.5561 | 11.2179 | 1.9575 | 1.4344 | 9.5561 | 1.4344 | 10.1499 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 6.0841 | 10.2211 | 11.2179 | 1.9575 | 1.4344 | 10.2211 | 1.4344 | 6.4123 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 5.7507 | 10.3877 | 31.3792 | 9.2759 | 6.768 | 10.3877 | 6.1854 | 10.7604 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 14.7134 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 11.043 | 15.68 | 30.3333 | 13.1144 | 9.5686 | 15.68 | 9.7958 | 15.68 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 13.535 | 21.285 | 33.7019 | 8.5111 | 6.21 | 21.285 | 6.7082 | 17.439 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 0.51579 | 2.9381 | 11.2179 | 1.9575 | 1.4344 | 2.9381 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.2939 | 8.4802 | 8.4802 | 8.4802 | 4.2939 | 8.4802 | 3.8465 | PP submitted, awaiting Clock Start date
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.6138 | 10.6138 | 20.5557 | 20.5557 | 19.2098 | 10.6138 | 19.2177 | 9.8578 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 2.0081 | 6.6451 | 29.2513 | 6.1516 | 4.4212 | 6.6451 | 3.7567 | 5.6289 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 12.9279 | 33.4279 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 5.5157 | 10.1527 | 32.4374 | 12.2884 | 8.8319 | 10.1527 | 8.9022 | 10.8219 | PP submitted, awaiting Clock Start date
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 4.5459 | 9.1829 | 11.2179 | 1.9575 | 1.4344 | 9.1829 | 1.4344 | 0 | Offer signed 27/08/2024
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 8.6585 | 19.2985 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 3.7638 | 7.2638 | 24.6012 | 12.5977 | 9.0542 | 7.2638 | 9.1136 | 8.37 | Offer with ENW, due to be signed 22/01/2025
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 5.876 | 14.6357 | 30.3079 | 13.2474 | 9.6657 | 14.6357 | 9.8568 | 6.6125 | Offer with ENW, due to be signed 11/03/2025
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 3.4577 | 8.6294 | 30.1118 | 12.788 | 9.3305 | 8.6294 | 9.4256 | 12.706 | Offer with ENW, due to be signed 22/01/2025
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 10.9837 | 16.2088 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | PP submitted, awaiting Clock Start date
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 8.914 | 13.414 | 27.8355 | 13.6831 | 9.8343 | 13.414 | 9.8081 | 10.2615 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 15.7501 | 15.7501 | 15.2123 | 5.4302 | 3.962 | 15.2123 | 3.8058 | 9.6649 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 9.2289 | 9.2289 | 23.2074 | 9.7278 | 7.0977 | 9.2289 | 6.7909 | 5.3989 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 0.76002 | 9.76 | 17.9015 | 17.9015 | 17.3189 | 9.76 | 17.1739 | 8.8706 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 0 | 7.2836 | 1.1992 | 0.86188 | 0 | 0.7451 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0 | 0 | 15.5363 | 8.7009 | 6.2535 | 0 | 4.4683 | 2.8737 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 7.037 | 11.174 | 11.2179 | 1.9575 | 1.4344 | 11.174 | 1.4344 | 8.2958 | Offer signed 24/12/2024
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.8954 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 9.4923 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Offer signed 24/12/2024
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 13.8963 | 34.8963 | 0.48697 | 0.078979 | 0.057625 | 0.48697 | 0.16545 | 1.3982 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.1987 | 17.1777 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 2.8436 | 5.3436 | 8.424 | 8.424 | 8.424 | 5.3436 | 8.424 | 5.5206 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 2.3258 | 22.8258 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 13.0021 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 5.8479 | 10.4849 | 22.5066 | 3.6503 | 2.6633 | 10.4849 | 2.09 | 9.5109 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.5568 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 8.0361 | 13.2261 | 30.7725 | 16.3627 | 11.9387 | 13.2261 | 12.1148 | 12.9781 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 15.4378 | 24.4378 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 2.974 | 2.974 | 26.8888 | 4.361 | 3.1819 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.427 | 8.747 | 11.2179 | 1.9575 | 1.4344 | 8.747 | 1.4344 | 8.4761 | Offer signed 24/12/2024
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 17.9193 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.9942 | 12.8942 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | PP submitted, awaiting Clock Start date
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 5.5565 | 12.9565 | 31.5852 | 10.1926 | 7.3256 | 12.9565 | 7.3076 | 14.6753 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 4.4934 | 7.9934 | 22.4112 | 11.0979 | 8.0973 | 7.9934 | 8.0328 | 8.3048 | Offer with ENW, due to be signed 22/01/2025
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 6.73 | 11.367 | 31.3411 | 12.8478 | 9.2339 | 11.367 | 9.2691 | 12.9036 | Offer with ENW, due to be signed 22/01/2025
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.8479 | 2.8479 | 22.1947 | 15.2312 | 11.1131 | 2.8479 | 11.1639 | 2.7039 | Offer signed 24/12/2024
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 9.3284 | 16.0184 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 3.1435 | 8.1435 | 24.4081 | 9.2368 | 6.7394 | 8.1435 | 5.9831 | 2.9543 | Offer with ENW, due to be signed 11/03/2025
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.6031 | 13.9049 | 18.6656 | 18.6656 | 17.1155 | 13.9049 | 17.154 | 12.6129 | Offer with ENW, due to be signed 11/03/2025
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0 | 0 | 24.012 | 13.2695 | 9.5371 | 0 | 5.1053 | 5.0492 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 4.757 | 10.757 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 9.12 | Offer with ENW, due to be signed 11/03/2025
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 5.1324 | 11.9324 | 14.2681 | 14.2681 | 14.2681 | 11.9324 | 7.0436 | 11.2916 | PP submitted, awaiting Clock Start date
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 5.7715 | 10.4085 | 26.0405 | 6.3933 | 4.6647 | 10.4085 | 2.9125 | 3.9899 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0.26281 | 1.2416 | 8.4614 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 3.7068 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6258 | 19.3058 | 27.6988 | 10.7173 | 7.8196 | 19.3058 | 7.0436 | 19.3058 | PP submitted, awaiting Clock Start date
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 4.1479 | 7.6479 | 11.2179 | 1.9575 | 1.4344 | 7.6479 | 1.4344 | 7.8631 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 6.7153 | 7 | 1.9575 | 1.4344 | 6.7153 | 1.4344 | 4.7605 | Offer signed 24/12/2024
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 2.6245 | 18.1909 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting Clock Start date
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.1536 | 15.5785 | 43.3786 | 8.5345 | 6.227 | 15.5785 | 1.845 | 13.1837 | PP submitted, awaiting Clock Start date
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.4823 | 4.8516 | 4.8516 | 4.8516 | 1.4823 | 4.8516 | 1.4303 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.3635 | 7.0005 | 23.0632 | 4.5987 | 3.3554 | 7.0005 | 2.296 | 3.1319 | PP submitted, offer due 16/04/2025
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.2053 | 8.5053 | 11.2179 | 1.9575 | 1.4344 | 8.5053 | 1.4344 | 8.1583 | Offer signed 24/12/2024
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.0804 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 2.289 | 6.926 | 32.4077 | 6.9115 | 4.9674 | 6.926 | 0.088852 | 0 | Offer signed 24/12/2024
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 1.8873 | 13.5703 | 11.528 | 8.4475 | 1.8873 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 7.353 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 1.548 | 9.028 | 32.4628 | 15.2777 | 10.9804 | 9.028 | 11.6712 | 8.928 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 5.876 | 15.7382 | 29.9539 | 12.5503 | 9.157 | 15.7382 | 9.1618 | 11.3246 | Offer with ENW, due to be signed 11/03/2025
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.3663 | 15.0033 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 5.9174 | 10.5544 | 11.2179 | 1.9575 | 1.4344 | 10.5544 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DICKINSON ST | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 5.876 | 11.4696 | 36.7251 | 12.5088 | 9.1268 | 11.4696 | 9.5067 | 5.4068 | Offer with ENW, due to be signed 11/03/2025
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.3769 | 13.0139 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 11/03/2025
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 0.66949 | 0.66949 | 11.2179 | 1.9575 | 1.4344 | 0.66949 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.7845 | 15.4445 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 6.9119 | 11.5489 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.4097 | Offer signed 27/08/2024
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.0255 | 14.6625 | 22.8446 | 3.7051 | 2.7033 | 14.6625 | 2.6715 | 15.6217 | Offer signed 27/08/2024
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 6.0671 | 12.5671 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 7.2779 | Offer signed 24/12/2024
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 19.9456 | 21.3456 | 10.5328 | 1.7341 | 1.2464 | 10.5328 | 0.99981 | 8.4492 | PP submitted, awaiting Clock Start date
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 10.9278 | 15.5648 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 27/08/2024
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0.077726 | 2.8786 | 2.8786 | 2.8786 | 0.077726 | 2.8786 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 2.5922 | 5.0922 | 14.6978 | 14.6978 | 11.9742 | 5.0922 | 12.6319 | 4.995 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.2201 | 14.2201 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 0 | 5.7026 | 21.1 | 3.6819 | 2.698 | 5.7026 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 2.974 | 2.974 | 28.9569 | 8.9029 | 6.5239 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 6.5382 | 11.1752 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 11.2006 | Offer with ENW, due to be signed 11/03/2025
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 10.1824 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 0 | 14.9243 | 19.0252 | 3.6819 | 2.698 | 14.9243 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 1.2618 | 14.0312 | 30.4491 | 15.8633 | 11.4013 | 14.0312 | 11.2192 | 5.6473 | Offer signed 27/08/2024
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 4.8793 | 11.0501 | 11.0501 | 11.0501 | 4.8793 | 11.0501 | 4.4257 | PP submitted, awaiting Clock Start date
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 12.8266 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 2.1063 | 8.6063 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 12.1782 | 12.5347 | 30.4947 | 12.2101 | 8.9088 | 12.5347 | 8.6697 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 0.7447 | 0.7447 | 14.6333 | 10.2743 | 7.5289 | 0.7447 | 9.0987 | 0.2593 | PP submitted, offer due 16/04/2025
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.4591 | 11.9591 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 1.2188 | 5.8558 | 32.1414 | 12.3675 | 9.0237 | 5.8558 | 8.9257 | 9.6892 | Offer signed 27/08/2024
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0 | 0 | 7.5611 | 7.5611 | 7.5611 | 0 | 7.4769 | 2.881 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 6.2572 | 18.2072 | 9.2697 | 1.5262 | 1.0969 | 9.2697 | 1.4212 | 12.0107 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.3598 | 12.9968 | 30.7974 | 5.374 | 3.938 | 12.9968 | 5.4751 | 12.055 | Offer signed 27/08/2024
GOLBORNE | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 0.74243 | 6.2424 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 4.2925 | 8.9295 | 29.9812 | 10.1565 | 7.2997 | 8.9295 | 7.0494 | 5.6473 | Offer signed 27/08/2024
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.2872 | 14.3872 | 24.7332 | 6.3948 | 4.6658 | 14.3872 | 5.885 | 14.3872 | PP submitted, awaiting Clock Start date
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.226 | 10.226 | 21.0097 | 19.9991 | 14.6551 | 10.226 | 19.5311 | 10.7263 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 8.8093 | 16.9293 | 19.4454 | 3.3901 | 2.4735 | 16.9293 | 1.1085 | 9.368 | PP submitted, awaiting Clock Start date
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 5.1213 | 9.7583 | 32.2668 | 15.6787 | 11.2686 | 9.7583 | 11.1508 | 10.8283 | PP submitted, awaiting Clock Start date
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 0 | 3.2261 | 33.5043 | 8.7657 | 6.3001 | 3.2261 | 5.6166 | 0.45951 | Offer with ENW, due to be signed 22/01/2025
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0 | 3.6514 | 21.3921 | 9.1301 | 6.6616 | 3.6514 | 4.1968 | 3.8848 | Offer signed 27/08/2024
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 1.7293 | 10.1549 | 32.3774 | 7.5686 | 5.5223 | 10.1549 | 5.7981 | 10.2071 | Offer signed 27/08/2024
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 12.2922 | 16.7922 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 15.2042 | 21.109 | 55.5263 | 9.9001 | 7.2234 | 21.109 | 6.8407 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 0 | 13.1505 | 21.1 | 3.6819 | 2.698 | 13.1505 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 12.0416 | 16.7619 | 7.6328 | 1.2567 | 0.9032 | 7.6328 | 0.83754 | 7.0779 | Offer signed 27/08/2024
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 0 | 0 | 21.3624 | 10.34 | 7.5444 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 7.5935 | 12.2305 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0 | 0 | 10.8975 | 10.8975 | 10.8975 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 5.6699 | 10.3069 | 31.6811 | 12.6595 | 9.2367 | 10.3069 | 9.5452 | 9.9239 | PP submitted, awaiting Clock Start date
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 11.192 | 15.832 | 30.4539 | 12.3439 | 9.0065 | 15.832 | 9.1946 | 15.552 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 2.82 | 7.12 | 11.2179 | 1.9575 | 1.4344 | 7.12 | 1.4344 | 7.187 | Offer signed 24/12/2024
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 1.4258 | 4.9258 | 15.8004 | 4.9061 | 3.5261 | 4.9258 | 3.4214 | 6.4802 | Offer signed 27/08/2024
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.291 | 6.791 | 13.0026 | 13.0026 | 13.0026 | 6.791 | 13.0026 | 6.7952 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 11.2015 | 15.7015 | 30.5328 | 16.9152 | 12.1573 | 15.7015 | 12.0132 | 15.4515 | Offer with ENW, due to be signed 22/01/2025
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 6.8033 | 12.3033 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.1069 | 19.3269 | 3.391 | 0.5583 | 0.40126 | 3.391 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.1069 | 19.3269 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 4.0459 | 7.5459 | 24.7522 | 10.2195 | 7.4565 | 7.5459 | 7.0425 | 7.7035 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 5.207 | 5.207 | 6.8624 | 1.9575 | 1.4344 | 5.207 | 1.4344 | 2.695 | Offer signed 24/12/2024
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.2144 | 17.4244 | 29.9937 | 9.0755 | 6.6217 | 17.4244 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 0 | 0 | 31.1274 | 9.5782 | 6.9885 | 0 | 7.1221 | 0 | Offer with ENW, due to be signed 22/01/2025
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0 | 0 | 27.7408 | 4.4992 | 3.2827 | 0 | 3.0681 | 0 | Offer with ENW, due to be signed 22/01/2025
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.44686 | 8.4469 | 13.2972 | 13.2972 | 13.2972 | 8.4469 | 13.2972 | 8.3367 | PP submitted, awaiting Clock Start date
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 12.9453 | 17.0823 | 14.6978 | 11.5093 | 8.272 | 14.6978 | 9.101 | 17.1039 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.6561 | 14.2931 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 10.1531 | 14.7901 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 6.0399 | 7.1711 | 16.123 | 2.6149 | 1.9079 | 7.1711 | 1.2885 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 4.5777 | 12.0777 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 3.0994 | 7.7364 | 21.3152 | 5.3738 | 3.8623 | 7.7364 | 3.7037 | 4.126 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 6.9262 | 7 | 1.9575 | 1.4344 | 6.9262 | 1.4344 | 7 | Offer signed 24/12/2024
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0.95096 | Offer signed 24/12/2024
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 5.6215 | 8.6289 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Offer signed 24/12/2024
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 2.974 | 2.974 | 26.6633 | 7.132 | 5.2037 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.7551 | 10.8921 | 11.2179 | 1.9575 | 1.4344 | 10.8921 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 3.337 | 6.837 | 11.2179 | 1.9575 | 1.4344 | 6.837 | 1.4344 | 6.5258 | Offer signed 24/12/2024
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 5.5232 | 9.0232 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 17.2503 | 13.3736 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.5327 | 11.1697 | 30.7974 | 5.374 | 3.938 | 11.1697 | 5.4751 | 11.4433 | Offer signed 27/08/2024
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.8125 | 17.1125 | 29.3612 | 13.56 | 9.8937 | 17.1125 | 7.0436 | 17.6125 | PP submitted, awaiting Clock Start date
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 0 | 15.9252 | 21.1 | 3.6819 | 2.698 | 15.9252 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 9.0341 | 12.6981 | 12.6981 | 12.6981 | 9.0341 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 3.1221 | 7.2621 | 11.2179 | 1.9575 | 1.4344 | 7.2621 | 1.4344 | 4.4053 | PP submitted, awaiting Clock Start date
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 7.3916 | 11.5286 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.3013 | 17.4383 | 29.8132 | 13.3347 | 9.7293 | 17.4383 | 7.0436 | 16.5205 | PP submitted, awaiting Clock Start date
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 6.2811 | 28.0218 | 9.3317 | 6.7069 | 6.2811 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 2.3127 | 4.8127 | 7 | 1.9575 | 1.4344 | 4.8127 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 12.5347 | 12.5347 | 45.8137 | 8.427 | 6.0566 | 12.5347 | 1.6009 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.81619 | 2.3162 | 3.1954 | 3.1954 | 3.1954 | 2.3162 | 3.1954 | 2.3112 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 6.1741 | 13.7662 | 13.7662 | 13.7662 | 6.1741 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.2241 | 5.7241 | 3.4566 | 3.4566 | 3.4566 | 3.4566 | 2.8987 | 2.8987 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 19.5904 | 10.2783 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 18.6543 | 13.2545 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 3.5567 | 5.9067 | 19.9589 | 11.3727 | 8.1738 | 5.9067 | 8.0695 | 0 | Offer signed 24/12/2024
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 0 | 10.8781 | 31.9515 | 12.5504 | 9.1571 | 10.8781 | 9.0797 | 10.8837 | Offer signed 27/08/2024
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 4.211 | 31.367 | 6.9245 | 5.0523 | 4.211 | 4.9077 | 0 | Offer with ENW, due to be signed 11/03/2025
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 0 | 14.3551 | 24.478 | 9.53 | 6.9533 | 14.3551 | 7.0795 | 15.6051 | Offer signed 27/08/2024
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 2.7658 | 2.974 | 33.1798 | 8.9029 | 6.5239 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 2.6245 | 15.0194 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting Clock Start date
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.3639 | 8.6289 | 19.6186 | 19.6186 | 19.6186 | 8.6289 | 19.6186 | 0 | Offer signed 24/12/2024
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 2.5861 | 6.0861 | 25.4427 | 13.7544 | 10.0356 | 6.0861 | 10.1941 | 6.1719 | Offer with ENW, due to be signed 22/01/2025
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 13.7639 | 21.549 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 3.4504 | 7 | 1.9575 | 1.4344 | 3.4504 | 1.4344 | 4.4466 | Offer signed 24/12/2024
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 16.5605 | 4.0762 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 2.0518 | 5.5518 | 25.0991 | 9.8649 | 7.1977 | 5.5518 | 6.9929 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 10.3372 | 14.9742 | 31.2344 | 7.8108 | 5.699 | 14.9742 | 5.7031 | 10.4658 | Offer with ENW, due to be signed 11/03/2025
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 0.66949 | 0.66949 | 11.2179 | 1.9575 | 1.4344 | 0.66949 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 2.3892 | 6.5262 | 27.2475 | 5.3434 | 3.8987 | 6.5262 | 2.8907 | 9.1882 | Offer with ENW, due to be signed 22/01/2025
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 1.8073 | 7.8073 | 35.2738 | 5.8076 | 4.174 | 7.8073 | 0.088852 | 0 | Offer signed 24/12/2024
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 0 | 16.7469 | 21.1 | 3.6819 | 2.698 | 16.7469 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 17.4206 | 19.6576 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.6576 | PP submitted, awaiting Clock Start date
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 0.72762 | 30.0909 | 10.1965 | 7.4396 | 0.72762 | 7.4513 | 1.5496 | Offer with ENW, due to be signed 22/01/2025
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0 | 0 | 7.1061 | 7.1061 | 7.1061 | 0 | 7.1061 | 0 | Offer with ENW, due to be signed 22/01/2025
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 10.1794 | 14.7794 | 24.6386 | 8.3748 | 6.1105 | 14.7794 | 6.5522 | 14.5624 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 8.9475 | 17.6711 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.358 | 7.1573 | 7.1573 | 7.1573 | 3.358 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 0 | 0 | 21.3624 | 12.8617 | 9.3843 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 2.974 | 2.974 | 26.9459 | 4.4364 | 3.1886 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 8.8016 | 11.6014 | 14.6978 | 14.6978 | 14.6978 | 11.6014 | 18.0835 | 11.4916 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 10.2974 | 14.9374 | 30.1883 | 10.3379 | 7.5428 | 14.9374 | 7.4802 | 14.0754 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 7.494 | 15.1549 | 2.4951 | 1.7933 | 7.494 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 6.6836 | 10.1836 | 11.2179 | 1.9575 | 1.4344 | 10.1836 | 1.4344 | 0 | Offer signed 27/08/2024
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 3.8631 | 7.3631 | 11.2179 | 1.9575 | 1.4344 | 7.3631 | 1.4344 | 5.0297 | PP submitted, awaiting Clock Start date
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 2.1231 | 5.6231 | 11.2179 | 1.9575 | 1.4344 | 5.6231 | 1.4344 | 8.9507 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 8.3041 | 12.1041 | 2.5359 | 0.44197 | 0.31765 | 2.5359 | 0.31765 | 2.6844 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 1.7166 | 5.2166 | 23.7167 | 9.1698 | 6.6905 | 5.2166 | 5.8695 | 0 | Offer with ENW, due to be signed 11/03/2025
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 4.0674 | 7 | 1.9575 | 1.4344 | 4.0674 | 1.4344 | 3.7702 | Offer signed 24/12/2024
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 14.8904 | 21.4377 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.3845 | 6.6985 | 27.9116 | 12.6818 | 9.1146 | 6.6985 | 9.1199 | 4.5253 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.8462 | 31.5971 | 10.2909 | 7.5085 | 2.8462 | 7.5673 | 1.6732 | Offer with ENW, due to be signed 22/01/2025
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 9.3376 | 13.9746 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 10.6685 | 15.3054 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.7054 | PP submitted, awaiting Clock Start date
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.642 | 14.262 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 1.4658 | 5.6058 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting Clock Start date
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 2.974 | 2.974 | 31.0839 | 8.9029 | 6.5239 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 0 | 3.8322 | 3.8322 | 3.8322 | 0 | 3.8322 | 2.0546 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 15.0523 | 7.0631 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.7563 | 15.5143 | 8.0566 | 5.374 | 3.938 | 8.0566 | 1.511 | 1.511 | Offer signed 27/08/2024
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 1.9905 | 1.9905 | 12.0025 | 8.9029 | 6.5239 | 1.9905 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 8.7634 | 12.9004 | 28.3704 | 11.1489 | 8.0129 | 12.9004 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 14.5974 | 4.7101 | 3.3853 | 0 | 3.841 | 8.6565 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 14.4183 | 10.2752 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.3747 | 22.8902 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 10.47 | 15.107 | 8.1098 | 1.3352 | 0.95965 | 8.1098 | 0.56343 | 4.7615 | Offer with ENW, due to be signed 22/01/2025
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 7.508 | 11.008 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 9.31 | Offer with ENW, due to be signed 11/03/2025
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 2.2913 | 7.2313 | 11.2179 | 1.9575 | 1.4344 | 7.2313 | 1.4344 | 10.0382 | PP submitted, awaiting Clock Start date
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 0 | 0 | 30.5974 | 12.4705 | 9.0988 | 0 | 9.1327 | 0 | Offer with ENW, due to be signed 22/01/2025
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 2.3632 | 5.8632 | 11.2179 | 1.9575 | 1.4344 | 5.8632 | 1.4344 | 5.886 | Offer signed 27/08/2024
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 8.7868 | 13.4238 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 13.2449 | 21.3337 | 6.6934 | 1.102 | 0.79205 | 6.6934 | 0.84345 | 7.1279 | PP submitted, awaiting Clock Start date
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0 | 8.8523 | 19.6031 | 19.6031 | 19.6031 | 8.8523 | 19.6031 | 8.983 | PP submitted, awaiting Clock Start date
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 14.6928 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 7.9823 | 12.1193 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 1.4954 | 10.4954 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting Clock Start date
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 5.876 | 16.5633 | 29.5281 | 8.4802 | 6.1874 | 16.5633 | 6.0414 | 15.0117 | Offer with ENW, due to be signed 11/03/2025
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 8.5018 | 22.7713 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 7.7571 | 11.5571 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 0 | 0 | 31.2648 | 9.1522 | 6.6777 | 0 | 6.7371 | 0 | Offer with ENW, due to be signed 22/01/2025
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 9.1791 | 11.1591 | 11.2179 | 1.9575 | 1.4344 | 11.1591 | 1.4344 | 6.9765 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 6.697 | 10.197 | 23.6228 | 13.2265 | 9.5061 | 10.197 | 9.4181 | 10.8112 | Offer with ENW, due to be signed 22/01/2025
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 11.2011 | 15.7011 | 26.8965 | 10.2743 | 7.5289 | 15.7011 | 9.0987 | 15.8281 | PP submitted, offer due 16/04/2025
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 0.66949 | 0.66949 | 2.6918 | 0.43658 | 0.31854 | 0.66949 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 11.301 | 15.938 | 30.2268 | 11.7701 | 8.5878 | 15.938 | 8.77 | 17.138 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 5.5826 | 10.2196 | 32.1779 | 7.9526 | 5.8024 | 10.2196 | 5.8553 | 6.3816 | Offer signed 24/12/2024
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 5.0473 | 12.6073 | 30.2531 | 12.323 | 8.9912 | 12.6073 | 8.8549 | 17.2513 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.2872 | 14.3872 | 24.7332 | 11.0926 | 8.0935 | 14.3872 | 9.5083 | 14.3872 | PP submitted, awaiting Clock Start date
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 7.051 | 9.0713 | 11.2179 | 1.9575 | 1.4344 | 9.0713 | 1.4344 | 0 | Offer signed 27/08/2024
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 8.6009 | 9.0009 | 43.9949 | 11.7803 | 8.4667 | 9.0009 | 8.7443 | 5.7413 | Offer signed 24/12/2024
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 5.4637 | 18.1637 | 34.9192 | 12.5889 | 9.1852 | 18.1637 | 8.8192 | 17.3639 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.6415 | 15.2785 | 30.169 | 15.9252 | 11.6195 | 15.2785 | 11.7382 | 14.2835 | PP submitted, awaiting Clock Start date
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 0 | 0 | 30.3545 | 9.8407 | 7.18 | 0 | 7.0914 | 0 | Offer with ENW, due to be signed 22/01/2025
RIBBLESDALE T13 & RIBBLESDALE T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 1.934 | 4.684 | 22.1282 | 15.8516 | 11.3928 | 4.684 | 11.8923 | 1.683 | PP submitted, awaiting Clock Start date
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 0.66949 | 0.66949 | 11.2179 | 1.9575 | 1.4344 | 0.66949 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 9.003 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 8.7641 | 8.8484 | 1.4568 | 1.047 | 8.7641 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 13.2755 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 18.2813 | 31.2813 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 0 | 14.7322 | 21.1 | 3.6819 | 2.698 | 14.7322 | 0 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 0 | 0 | 24.0007 | 10.8422 | 7.7925 | 0 | 7.5834 | 0 | Offer with ENW, due to be signed 22/01/2025
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 0 | 3.109 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 16/04/2025
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 8.9049 | 13.5419 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 11.4457 | 16.0857 | 31.0489 | 8.4608 | 6.1732 | 16.0857 | 6.5677 | 14.7385 | PP submitted, awaiting Clock Start date
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 1.5401 | 1.5401 | 12.01 | 12.01 | 12.01 | 1.5401 | 12.01 | 1.3941 | PP submitted, awaiting Clock Start date
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 16.67 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 11.68 | 16.18 | 30.3 | 17.8186 | 12.8066 | 16.18
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 8.2924 | 12.7924 | 30.2683 | 9.98 | 7.1728 | 12.7924 | 7.2924 | 14.3266 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.1832 | 3.6832 | 6.4667 | 1.9575 | 1.4344 | 3.6832 | 1.4344 | 3.6656 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0 | 0.36018 | 1.9438 | 1.9438 | 1.4344 | 0.36018 | 1.4344 | 1.1732 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 10.0598 | 19.5532 | 19.5532 | 19.1843 | 10.0598 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0 | 0 | 4.9054 | 4.9054 | 4.9054 | 0 | 4.9054 | 1.1883 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.26801 | 7.768 | 13.3716 | 13.3716 | 13.3716 | 7.768 | 13.3716 | 7.6618 | PP submitted, awaiting Clock Start date
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.0585 | 7.4085 | 32.0548 | 26.4239 | 18.9914 | 7.4085 | 18.9995 | 5.2353 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 4.228 | 9.728 | 32.1479 | 10.7137 | 7.817 | 9.728 | 8.0106 | 5.397 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 0 | 0 | 12.2325 | 12.2325 | 12.2325 | 0 | 12.2325 | 7.0318 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 9.6466 | 14.2836 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.154 | 23.7448 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 16.1058 | 38.4444 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 4.298 | 8.935 | 11.2179 | 1.9059 | 1.3698 | 8.935 | 1.3976 | 7.809 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 0 | 0 | 14.5974 | 14.5974 | 12.3443 | 0 | 17.7881 | 13.3736 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 5.8335 | 7.8335 | 14.6978 | 14.6978 | 11.7573 | 7.8335 | 12.7115 | 7.3459 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 6.865 | 11.502 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 27/08/2024
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 8.1563 | 8.1563 | 11.2179 | 1.9575 | 1.4344 | 8.1563 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.4307 | 18.2303 | 29.4531 | 11.4383 | 8.221 | 18.2303 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.529 | 6.666 | 11.2179 | 1.9575 | 1.4344 | 6.666 | 1.4344 | 0 | PP submitted, awaiting Clock Start date
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 5.2005 | 5.2005 | 11.2179 | 1.9575 | 1.4344 | 5.2005 | 1.4344 | 5.2215 | Offer signed 24/12/2024
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 25.7295 | 32.7295 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 6.412 | 9.912 | 23.6188 | 13.3943 | 9.7728 | 9.912 | 4.1691 | 9.6296 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 2.6245 | 18.7784 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting Clock Start date
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 5.5189 | 10.1189 | 16.6276 | 2.6968 | 1.9676 | 10.1189 | 2.1114 | 6.2955 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 9.1032 | 12.6032 | 23.0658 | 9.7385 | 7.1055 | 12.6032 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 9.6203 | 14.2573 | 29.2752 | 10.5824 | 7.7212 | 14.2573 | 7.7148 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 7.1664 | 10.6664 | 11.2179 | 1.9575 | 1.4344 | 10.6664 | 1.4344 | 10.0664 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 13.7705 | 18.2303 | 30.1228 | 12.8932 | 9.4072 | 18.2303 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.1817 | 10.6817 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0 | 0 | 2.6844 | 0.44197 | 0.31765 | 0 | 1.9914 | 1.9914 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 11.5685 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 5.2912 | 9.4282 | 20.7413 | 3.3639 | 2.4544 | 9.4282 | 2.4384 | 6.5078 | PP submitted, awaiting Clock Start date
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 7.9793 | 14.9793 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 9.7731 | 26.7731 | 26.0484 | 4.2887 | 3.0823 | 26.0484 | 2.782 | 23.5098 | PP submitted, awaiting Clock Start date
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.6986 | 18.1986 | 30.2092 | 14.9198 | 10.7232 | 18.1986 | 10.853 | 18.1986 | Offer signed 24/12/2024
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 7.1554 | 11.7924 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 8.916 | 13.053 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0 | 0 | 20.8292 | 7.442 | 5.3487 | 0 | 0.31765 | 2.6844 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 4.6961 | 15.3961 | 29.77 | 10.0667 | 7.3449 | 15.3961 | 7.3789 | 14.5981 | Offer signed 24/12/2024
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 17.6053 | 26.4 | 5.8 | 1.9575 | 1.4344 | 5.8
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 8.6442 | 11.7812 | 11.2179 | 1.8977 | 1.3639 | 11.2179 | 0.31765 | 2.6844 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 2.974 | 2.974 | 33.4932 | 8.9029 | 6.5239 | 2.974 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 7.3565 | 14.3565 | 22.3705 | 7.7125 | 5.6272 | 14.3565 | 5.7122 | 14.3365 | Offer with ENW, due to be signed 11/03/2025
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 6.2399 | 11.4899 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | PP submitted, awaiting Clock Start date
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 20.0999 | 20.0999 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 23.5237 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 24/12/2024
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 7.3748 | 11.5118 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 5.727 | 8.727 | 16.3552 | 10.1663 | 7.3067 | 8.727 | 7.6223 | 7.75 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 1.9788 | 6.6158 | 11.2179 | 1.9575 | 1.4344 | 6.6158 | 1.4344 | 9.7198 | Offer signed 24/12/2024
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 0 | 6.8611 | 22.0084 | 11.0676 | 7.9545 | 6.8611 | 8.1328 | 6.6945 | Offer signed 27/08/2024
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 11.1241 | 15.7611 | 28.9446 | 7.9265 | 5.7834 | 15.7611 | 5.7691 | 14.4783 | Offer with ENW, due to be signed 11/03/2025
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 5.1043 | 25.5112 | 8.2663 | 6.0313 | 5.1043 | 4.6312 | 4.9475 | Offer with ENW, due to be signed 22/01/2025
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.4371 | 10.9371 | 11.2179 | 1.9575 | 1.4344 | 10.9371 | 1.4344 | 10.9371 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 5.8835 | 10.5205 | 31.4551 | 7.9706 | 5.8156 | 10.5205 | 5.5739 | 0 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 0 | 0 | 21.3624 | 12.6267 | 9.2128 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 14.6569 | 19.2939 | 29.365 | 13.0577 | 9.5272 | 19.2939 | 9.344 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 2.0975 | 2.0975 | 28.4979 | 12.4455 | 8.9448 | 2.0975 | 1.3561 | 10.6051 | Offer signed 27/08/2024
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 11.5011 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed 24/12/2024
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 13.7613 | 18.3983 | 30.177 | 12.7136 | 9.2762 | 18.3983 | 8.8768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 12.7289 | 17.3659 | 30.2639 | 13.4536 | 9.8161 | 17.3659 | 10.1945 | 7.7239 | PP submitted, awaiting Clock Start date
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7897 | 10.7897 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 8.6933 | Offer with ENW, due to be signed 11/03/2025
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0 | 4.4346 | 11.3869 | 1.8748 | 1.3474 | 4.4346 | 0.088852 | 0 | Offer signed 24/12/2024
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 5.6023 | 8.7386 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 8.5757 | 13.2127 | 28.3048 | 7.9601 | 5.721 | 13.2127 | 5.5392 | 11.0853 | PP submitted, awaiting Clock Start date
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 2.5842 | 11.7212 | 8.852 | 1.9575 | 1.4344 | 8.852 | 1.4344 | 10.576 | Offer with ENW, due to be signed 11/03/2025
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 5.5937 | 23.0587 | 19.6401 | 14.1157 | 5.5937 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.775 | 9.275 | 23.9575 | 14.5159 | 10.4329 | 9.275 | 10.3146 | 9.0214 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 4.6744 | 6.1744 | 10.5081 | 4.5517 | 3.321 | 6.1744 | 3.1391 | 5.9064 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0 | 2.2795 | 7 | 1.9575 | 1.4344 | 2.2795 | 1.4344 | 0.21045 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 9.363 | 14 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.4046 | 5.9046 | 25.3471 | 13.0352 | 9.5108 | 5.9046 | 9.2635 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 6.9548 | 11.0918 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 4.8885 | 8.3885 | 5.8 | 1.9575 | 1.4344 | 5.8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 10.0598 | 30.4268 | 20.041 | 14.4039 | 10.0598 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 5.4547 | 8.9547 | 18.0363 | 6.6776 | 4.8722 | 8.9547 | 2.1791 | 7.5047 | Offer with ENW, due to be signed 22/01/2025
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.7832 | 6.2832 | 8.852 | 1.9575 | 1.4344 | 6.2832 | 1.4344 | 6.0832 | Offer with ENW, due to be signed 11/03/2025
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 8.1563 | 8.1563 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | PP submitted, awaiting Clock Start date
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.2182 | 8.7182 | 24.1055 | 14.3468 | 10.4678 | 8.7182 | 10.5673 | 8.8316 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0 | 0 | 30.1487 | 14.0026 | 10.0639 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 1.2416 | 1.2416 | 11.2179 | 1.9575 | 1.4344 | 1.2416 | 1.5151 | 2.7595 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 1.0021 | 4.5021 | 5.8 | 1.9575 | 1.4344 | 4.5021 | 1.4344 | 0.86929 | Offer with ENW, due to be signed 11/03/2025
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 0 | 0 | 10.7369 | 1.7677 | 1.2705 | 0 | 1.0921 | 0 | Offer with ENW, due to be signed 22/01/2025
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 10.6754 | 14.6754 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 8.8855 | 13.5225 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 1.7293 | 11.9477 | 26.1692 | 10.8659 | 7.9281 | 11.9477 | 7.7377 | 8.7753 | Offer signed 27/08/2024
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0 | 0 | 30.4446 | 15.243 | 10.9555 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 6.5082 | 12.8478 | 12.8478 | 12.8478 | 6.5082 | 0 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 51.1004 | 69.1004 | 142.4601 | 46.9376 | 69.1004 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 17.361 | 29.361 | 91.3244 | 27.3133 | 29.361 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Offer signed 24/12/2024
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 53.2922 | 71.2922 | 149.5819 | 49.023 | 71.2922 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | PP submitted, awaiting Clock Start date
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 8.6289 | 8.6289 | 119.9397 | 27.7947 | 8.6289 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Offer signed 24/12/2024
BARROW | 33 | HARKER | 319709 | 470489 | 37.4738 | 63.4738 | 60.4024 | 10.958 | 60.4024 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
BARTON | 33 | CARRINGTON | 376758 | 397174 | 52.2543 | 71.8495 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | PP submitted, awaiting Clock Start date
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 12.5347 | 12.5347 | 54.6806 | 22.9407 | 12.5347 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 36.6198 | 36.6198 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 36.1084 | 36.1084 | 68.8709 | 39.2155 | 36.1084 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 39.5005 | 40.3405 | 119.4893 | 35.0575 | 40.3405 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 5.876 | 55.3198 | 152.6811 | 48.154 | 55.3198 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 17.7431 | 30.4353 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Offer signed 24/12/2024
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 63.7996 | 63.7996 | 80.2594 | 29.1314 | 63.7996 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
BURY | 33 | KEARSLEY | 380272 | 411184 | 28.1902 | 28.1902 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Offer signed 24/12/2024
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 2.0975 | 2.0975 | 88.4788 | 44.9398 | 2.0975 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Offer signed 27/08/2024
CARLISLE | 33 | HARKER | 338655 | 556583 | 19.8328 | 41.0328 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 11.1089 | 32.1089 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | PP submitted, awaiting Clock Start date
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 46.2918 | 46.2918 | 103.112 | 37.5146 | 46.2918 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 2.974 | 2.974 | 48.5317 | 8.8044 | 2.974 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 36.1403 | 36.1403 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Offer signed 27/08/2024
EGREMONT | 33 | HARKER | 301070 | 513074 | 32.6928 | 32.6928 | 14.6978 | 14.6978 | 14.6978 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 23.5237 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Offer signed 24/12/2024
GOLBORNE | 33 | BOLD | 360607 | 397690 | 34.2375 | 52.2375 | 62.8415 | 11.4004 | 52.2375 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 21.109 | 21.109 | 84.0206 | 29.7558 | 21.109 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 37.1173 | 55.1173 | 137.0032 | 36.7739 | 55.1173 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 30.2422 | 92.2422 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Offer signed 27/08/2024
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 38.0422 | 51.8422 | 69.8986 | 21.0907 | 51.8422 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | PP submitted, awaiting Clock Start date
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 32.408 | 32.408 | 29.2951 | 5.3146 | 29.2951 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Offer signed 27/08/2024
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 25.5682 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Offer signed 24/12/2024
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 10.0598 | 96.2749 | 26.0403 | 10.0598 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 1.2416 | 1.2416 | 10.6707 | 1.9358 | 1.2416 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 12.6725 | 27.6365 | 124.2442 | 32.9102 | 27.6365 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 4.5214 | 22.5214 | 149.1089 | 39.0323 | 22.5214 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 0 | 46.0948 | 20.0707 | 3.6412 | 20.0707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 18.2303 | 18.2303 | 42.8677 | 40.3217 | 18.2303 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 8.1563 | 8.1563 | 10.6707 | 1.9358 | 8.1563 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | PP submitted, awaiting Clock Start date
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 17.6053 | 42.8053 | 5.5769 | 1.9358 | 5.5769 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
NELSON | 33 | PADIHAM | 385989 | 438643 | 2.6245 | 24.0373 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | PP submitted, awaiting Clock Start date
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 20.5875 | 20.5875 | 53.1931 | 53.1931 | 20.5875 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Offer signed 27/08/2024
ORRELL | 33 | KIRKBY | 352784 | 404565 | 0 | 19.447 | 104.8901 | 43.9872 | 19.447 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Offer signed 27/08/2024
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 13.2449 | 47.1067 | 139.7763 | 31.4863 | 47.1067 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | PP submitted, awaiting Clock Start date
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 0 | 0 | 21.3624 | 21.3624 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PENRITH | 33 | HUTTON | 349996 | 530398 | 0 | 0 | 14.5974 | 14.5974 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 0.66949 | 0.66949 | 10.6707 | 1.9358 | 0.66949 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 44.1553 | 62.4516 | 145.8409 | 32.765 | 62.4516 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 75.7366 | 111.7366 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 47.2333 | 59.2333 | 94.6521 | 40.5916 | 59.2333 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 42.092 | 53.6903 | 106.8182 | 53.3009 | 53.6903 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | PP submitted, awaiting Clock Start date
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 16.134 | 93.1126 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 33 | CARRINGTON | 378726 | 392892 | 24.5357 | 24.5357 | 78.4545 | 48.5518 | 24.5357 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | PP submitted, awaiting Clock Start date
SANDGATE | 33 | HARKER | 321492 | 468870 | 37.4738 | 63.4738 | 114.7732 | 20.8217 | 63.4738 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SHAP | 33 | HUTTON | 356910 | 513357 | 0 | 0 | 14.5974 | 14.5974 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
SIDDICK | 33 | HARKER | 300332 | 530823 | 37.9365 | 82.0365 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 22.7713 | 22.7713 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
STAINBURN | 33 | HARKER | 302535 | 529330 | 37.9365 | 82.0365 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 13.3312 | 59.958 | 131.4503 | 33.6544 | 59.958 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 128.7068 | 171.6463 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Offer signed 27/08/2024
THORNTON | 33 | STANAH | 334559 | 443368 | 12.1341 | 24.1341 | 26.8965 | 10.1606 | 24.1341 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | PP submitted, offer due 16/04/2025
ULVERSTON | 33 | HARKER | 327495 | 477808 | 30.7788 | 30.7788 | 35.2954 | 19.7779 | 30.7788 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 0 | 0 | 88.1369 | 16.2805 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 16.2001 | 52.7001 | 8.5115 | 1.9358 | 8.5115 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 19.8801 | 19.8801 | 88.0127 | 24.9991 | 19.8801 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Offer signed 24/12/2024
WIGAN | 33 | KIRKBY | 358343 | 404626 | 1.7293 | 40.7293 | 87.9264 | 35.3553 | 40.7293 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Offer signed 27/08/2024
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0 | 0 | 53.4316 | 20.6677 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date

## 6)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | 0 | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 282 | 0 | C | 0 | 426.2 | 3 | Offer with ENW, due to be signed 22/01/2025
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 0 | 0 | C | 4 | 199 | 5.13 | PP submitted, awaiting Clock Start date
HARKER | HARKER | 765.4 | 88 | 0 | 931.8 | 0 | C | 504.6 | 1785.2 | 0 | Offer signed 20/11/2024.Another parrallel submission made, offer due 15/02/2025. Another parrallel submission made, awaiting Clock start date
HUTTON | HUTTON | 47.9 | 53 | 0 | 151 | 0 | D | 233.8 | 251.9 | 0 | Offer with ENW, due to be signed 16/04/2025. Another PP submitted , awaiting Clock Start date.
HEYSHAM | HEYSHAM | 292.6 | 0 | 109 | 21.5 | 0 | C | 123.9 | 423.1 | 0 | Offer with ENW, due to be signed 06/09/2024- now extended to address move to Middleton .Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
KEARSLEY | KEARSLEY | 57.9 | 264.7 | 11 | 35 | 0 | C | 0 | 368.6 | 3 | Offer signed 24/12/2024
KIRKBY | KIRKBY | 6 | 146.4 | 0 | 80.9 | 0 | D | 0 | 233.3 | 3 | Offer signed 27/08/2024
MACCLESFIELD | MACCLESFIELD | 27.9 | 30 | 0 | 0 | 0 | C | 7.5 | 57.9 | 2.57 | PP submitted, awaiting Clock Start date
PADIHAM | PADIHAM | 35.5 | 135.1 | 219.9 | 164.9 | 0 | D | 7 | 555.4 | TBC | PP submitted, awaiting Clock Start date
PENWORTHAM | PENWORTHAM | 187.9 | 601.1 | 67.6 | 109.2 | 144 | D | 184.9 | 1109.8 | 9.21 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ROCHDALE | ROCHDALE | 204.1 | 179.1 | 35 | 191.3 | 0 | C | 184.9 | 639.5 | 3 | Offer signed 26/09/2024.PP submitted, offer due 13/02/2025.Another PP submitted,offer due 06/05/25
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 649.7 | 0 | C | 0 | 753.2 | 0 | Offer with ENW, due to be signed 11/03/2025
STALYBRIDGE | STALYBRIDGE | 58.3 | 236.8 | 0 | 50 | 0 | C | 0 | 345.1 | 0.591 | Offer signed 27/08/2024
STANAH | STANAH | 195.9 | 142 | 0 | 0 | 0 | C | 50 | 387.9 | 3.01 | PP submitted, offer due 16/04/2025
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 51.9 | 0 | D | 0 | 161 | 3 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WHITEGATE | WHITEGATE | 32 | 219.8 | 0 | 128.2 | 0 | C | 0 | 380 | 3.09 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application. D. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New GSPs have now been trigged by the latest Project progression return by ESO.