## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2025-03-25
This version is 499 days old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2024-12-08
This version is 606 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 0 | 11.6548 | 21.0205 | 3.668 | 2.6879 | 11.6548 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 9.2924 | 15.9824 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0 | 3.3047 | 3.3047 | 3.3047 | 0 | 3.2626 | 1.1073 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 9.8759 | 29.6287 | 25.1329 | 18.0635 | 9.8759 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 0 | 3.4339 | 32.3302 | 6.2209 | 4.5389 | 3.4339 | 4.8939 | 0.33304 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 5.9053 | 10.6553 | 19.2839 | 19.2839 | 15.6011 | 10.6553 | 15.7536 | 7.6053 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 3.6524 | 9.1524 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 5.0789 | 8.0789 | 21.7548 | 9.4543 | 6.8981 | 8.0789 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0.47844 | 5.4784 | 11.2179 | 1.9575 | 1.4344 | 5.4784 | 1.4344 | 0 | Offer signed 27/08/2024
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 9.8759 | 18.3845 | 18.3845 | 18.3845 | 9.8759 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 0.94597 | 26.2485 | 8.5806 | 6.2607 | 0.94597 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.8738 | 1.8738 | 5.57 | 1.9575 | 1.4344 | 1.8738 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 9.5983 | 13.7383 | 28.8941 | 8.5447 | 6.2345 | 13.7383 | 6.5315 | 13.4847 | PP submitted, offer due 16/04/2025
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 4.9687 | 9.1057 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9141 | 11.6641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 2.4011 | 2.4011 | 31.4391 | 10.0925 | 7.3637 | 2.4011 | 1.3561 | 10.6051 | Offer signed 27/08/2024
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 1.548 | 8.528 | 11.7207 | 6.3609 | 4.5717 | 8.528 | 6.4697 | 8.428 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92953 | 1.6295 | 3.9789 | 3.9789 | 3.9789 | 1.6295 | 3.9789 | 1.6295 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 3.4518 | 5.4518 | 7 | 1.9575 | 1.4344 | 5.4518 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 6.3779 | 8.6289 | 29.5361 | 4.8629 | 3.4951 | 8.6289 | 3.7461 | 0 | Offer signed 24/12/2024
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 5.3292 | 8.8292 | 22.71 | 13.1802 | 9.6166 | 8.8292 | 9.6723 | 7.1892 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 4.0415 | 4.0415 | 11.2179 | 1.9575 | 1.4344 | 4.0415 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 3.6678 | 8.3048 | 30.0013 | 9.7517 | 7.0087 | 8.3048 | 7.6584 | 8.6278 | PP submitted, offer due 16/04/2025
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 5.2549 | 9.3919 | 11.2179 | 1.9575 | 1.4344 | 9.3919 | 1.4344 | 10.2623 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 3.1045 | 11.2179 | 1.9575 | 1.4344 | 3.1045 | 1.4344 | 9.8525 | Offer signed 24/12/2024
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.8644 | 18.3644 | 21.1384 | 8.9772 | 6.5784 | 18.3644 | 8.0292 | 18.3194 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 2.1461 | 8.3961 | 11.2179 | 1.9575 | 1.4344 | 8.3961 | 1.4344 | 10.2441 | PP submitted, offer due 16/04/2025
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 4.9221 | 8.6289 | 28.5003 | 10.1005 | 7.2595 | 8.6289 | 7.2768 | 0 | Offer signed 24/12/2024
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.1244 | 10.6244 | 23.1258 | 11.5628 | 8.4366 | 10.6244 | 9.5768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.8921 | 9.8921 | 10.244 | 1.9575 | 1.4344 | 9.8921 | 1.4344 | 9.8921 | Offer with ENW, due to be signed 11/03/2025
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 5.2692 | 7.259 | 7.259 | 7.259 | 5.2692 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 5.1555 | 9.7925 | 11.2179 | 1.9575 | 1.4344 | 9.7925 | 1.4344 | 10.1499 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 6.0841 | 10.2211 | 11.2179 | 1.9575 | 1.4344 | 10.2211 | 1.4344 | 6.4123 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 5.7507 | 10.3877 | 31.3792 | 9.2764 | 6.7683 | 10.3877 | 6.1854 | 10.7604 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 10.4232 | 15.0602 | 30.3333 | 13.1252 | 9.5765 | 15.0602 | 9.7958 | 15.68 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 13.535 | 21.285 | 33.7019 | 8.5039 | 6.2047 | 21.285 | 6.7082 | 17.439 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 0.50229 | 2.9246 | 11.2179 | 1.9575 | 1.4344 | 2.9246 | 1.4344 | 0 | PP submitted, offer due 09/04/2025
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.2939 | 8.4802 | 8.4802 | 8.4802 | 4.2939 | 8.4802 | 3.8465 | PP submitted, offer due 12/05/2025
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.6138 | 10.6138 | 20.5557 | 20.5557 | 19.2109 | 10.6138 | 19.2177 | 9.8578 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 1.8989 | 6.5359 | 29.2513 | 6.152 | 4.4215 | 6.5359 | 3.7567 | 5.6289 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 12.9279 | 33.4279 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 5.5157 | 10.1527 | 32.4374 | 12.2502 | 8.8045 | 10.1527 | 8.9022 | 10.8219 | PP submitted, offer due 16/04/2025
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 4.5315 | 9.1685 | 11.2179 | 1.9575 | 1.4344 | 9.1685 | 1.4344 | 0 | Offer signed 27/08/2024
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 8.6585 | 19.2985 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 3.7638 | 7.2638 | 24.6012 | 12.6028 | 9.0579 | 7.2638 | 9.1136 | 8.37 | Offer with ENW, due to be signed 22/01/2025
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 0 | 8.3585 | 30.3079 | 13.2607 | 9.6754 | 8.3585 | 9.8568 | 6.6125 | Offer with ENW, due to be signed 11/03/2025
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 6.1577 | 11.3294 | 30.1118 | 12.7939 | 9.3347 | 11.3294 | 9.4256 | 12.706 | Offer with ENW, due to be signed 22/01/2025
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 10.9837 | 16.2088 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | PP submitted, offer due 16/04/2025
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 8.914 | 13.414 | 27.8355 | 13.683 | 9.8342 | 13.414 | 9.8081 | 10.2615 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 15.7501 | 15.7501 | 15.2123 | 5.2456 | 3.8274 | 15.2123 | 3.8058 | 9.6649 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 9.2289 | 9.2289 | 23.2074 | 9.7485 | 7.1128 | 9.2289 | 6.7909 | 5.3989 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 0.76002 | 9.76 | 17.9015 | 17.9015 | 17.2674 | 9.76 | 17.1739 | 8.8706 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 0 | 7.3615 | 1.212 | 0.8711 | 0 | 0.7451 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0 | 0 | 15.5363 | 8.7177 | 6.2656 | 0 | 4.4683 | 2.8737 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 7.037 | 11.174 | 11.2179 | 1.9575 | 1.4344 | 11.174 | 1.4344 | 8.2958 | Offer signed 24/12/2024
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.8954 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 9.4923 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Offer signed 24/12/2024
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 11.4705 | 32.4705 | 0.49975 | 0.081053 | 0.059139 | 0.49975 | 0.16545 | 1.3982 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.1987 | 17.1777 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 2.7356 | 5.2356 | 8.424 | 8.424 | 8.424 | 5.2356 | 8.424 | 5.5206 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 3.3638 | 23.8638 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 13.0021 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 5.5911 | 10.2281 | 22.5214 | 3.6527 | 2.6651 | 10.2281 | 2.09 | 9.5109 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.5568 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 8.0361 | 13.2261 | 30.7725 | 16.3685 | 11.9429 | 13.2261 | 12.1148 | 12.9781 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 4.4086 | 13.4086 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 2.4484 | 2.4484 | 26.8923 | 4.3615 | 3.1823 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.427 | 8.747 | 11.2179 | 1.9575 | 1.4344 | 8.747 | 1.4344 | 8.4761 | Offer signed 24/12/2024
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 0.526 | 11.426 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | PP submitted, offer due 16/04/2025
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 5.5565 | 12.9565 | 31.5852 | 8.9772 | 6.5784 | 12.9565 | 7.3076 | 14.6753 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 3.5934 | 7.0934 | 22.4112 | 11.0964 | 8.0962 | 7.0934 | 8.0328 | 8.3048 | Offer with ENW, due to be signed 22/01/2025
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 6.73 | 11.367 | 31.3411 | 12.8097 | 9.2066 | 11.367 | 9.2691 | 12.9036 | Offer with ENW, due to be signed 22/01/2025
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.8479 | 2.8479 | 22.1947 | 15.2378 | 11.1179 | 2.8479 | 11.1639 | 2.7039 | Offer signed 24/12/2024
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 9.2924 | 15.9824 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 0.63731 | 5.6373 | 24.4081 | 9.2531 | 6.7513 | 5.6373 | 5.9831 | 2.9543 | Offer with ENW, due to be signed 11/03/2025
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 3.6262 | 13.3529 | 18.6656 | 18.6656 | 17.1185 | 13.3529 | 17.154 | 12.6129 | Offer with ENW, due to be signed 11/03/2025
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0 | 0 | 24.012 | 13.2866 | 9.5494 | 0 | 5.1053 | 5.0492 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 4.5914 | 10.5914 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 9.12 | Offer with ENW, due to be signed 11/03/2025
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 5.1324 | 11.9324 | 14.2681 | 14.2681 | 14.2681 | 11.9324 | 7.0436 | 11.2916 | PP submitted, offer due 12/05/2025
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 5.7715 | 10.4085 | 26.0405 | 6.3994 | 4.6692 | 10.4085 | 2.9125 | 3.9899 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0.26281 | 1.0391 | 8.4614 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 3.7068 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6258 | 19.3058 | 27.6988 | 10.7059 | 7.8114 | 19.3058 | 7.0436 | 19.3058 | PP submitted, offer due 12/05/2025
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 4.1479 | 7.6479 | 11.2179 | 1.9575 | 1.4344 | 7.6479 | 1.4344 | 7.8631 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 6.7153 | 7 | 1.9575 | 1.4344 | 6.7153 | 1.4344 | 4.7605 | Offer signed 24/12/2024
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 2.5645 | 18.1909 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 12/05/2025
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.1536 | 15.5785 | 43.3786 | 8.5347 | 6.2271 | 15.5785 | 1.845 | 13.1837 | PP submitted, offer due 12/05/2025
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.4823 | 4.8516 | 4.8516 | 4.8516 | 1.4823 | 4.8516 | 1.4303 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.3635 | 7.0005 | 23.0632 | 4.6068 | 3.3612 | 7.0005 | 2.296 | 3.1319 | PP submitted, offer due 16/04/2025
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.2053 | 8.5053 | 11.2179 | 1.9575 | 1.4344 | 8.5053 | 1.4344 | 8.1583 | Offer signed 24/12/2024
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.0804 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 2.289 | 6.926 | 32.4077 | 6.9375 | 4.9861 | 6.926 | 0.088852 | 0 | Offer signed 24/12/2024
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 1.8873 | 13.5703 | 10.9651 | 8.0351 | 1.8873 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 7.353 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 1.548 | 9.028 | 32.4628 | 15.0551 | 10.8204 | 9.028 | 11.6712 | 8.928 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 0 | 11.075 | 29.9539 | 12.5509 | 9.1575 | 11.075 | 9.1618 | 11.3246 | Offer with ENW, due to be signed 11/03/2025
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.3663 | 15.0033 | 0.37436 | 0.065324 | 0.047869 | 0.37436 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 5.9174 | 10.5544 | 0.37436 | 0.065324 | 0.047869 | 0.37436 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DICKINSON ST | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 0 | 4.9908 | 36.7251 | 12.4979 | 9.1188 | 4.9908 | 9.5067 | 5.4068 | Offer with ENW, due to be signed 11/03/2025
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 7.1769 | 11.8139 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 11.2179 | Offer with ENW, due to be signed 11/03/2025
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 4.0415 | 4.0415 | 11.2179 | 1.9575 | 1.4344 | 4.0415 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.5745 | 15.2345 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 6.9119 | 11.5489 | 0.37436 | 0.065324 | 0.047869 | 0.37436 | 1.4344 | 9.4097 | Offer signed 27/08/2024
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.0255 | 14.6625 | 22.8682 | 3.7089 | 2.7061 | 14.6625 | 2.6715 | 15.6217 | Offer signed 27/08/2024
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 5.5871 | 12.0871 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 7.2779 | Offer signed 24/12/2024
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 12.0808 | 13.4808 | 6.9508 | 1.1444 | 0.8225 | 6.9508 | 0.99981 | 8.4492 | PP submitted, offer due 16/04/2025
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 5.8164 | 10.4534 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 27/08/2024
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0.077726 | 2.8786 | 2.8786 | 2.8786 | 0.077726 | 2.8786 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 1.7942 | 4.2942 | 14.6978 | 14.6978 | 11.9848 | 4.2942 | 12.6319 | 4.995 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.2201 | 14.2201 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 0 | 6.6146 | 21.0205 | 3.668 | 2.6879 | 6.6146 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 2.4484 | 2.4484 | 28.9569 | 8.9114 | 6.5302 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 6.5382 | 11.1752 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 11.2006 | Offer with ENW, due to be signed 11/03/2025
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 10.6 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 0 | 14.9243 | 19.0252 | 3.668 | 2.6879 | 14.9243 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 1.2618 | 14.0312 | 30.4491 | 15.866 | 11.4032 | 14.0312 | 11.2192 | 5.6473 | Offer signed 27/08/2024
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 4.8793 | 11.0501 | 11.0501 | 11.0501 | 4.8793 | 11.0501 | 4.4257 | PP submitted, offer due 12/05/2025
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 2.1063 | 8.6063 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 12.1782 | 12.2191 | 30.4947 | 12.2181 | 8.9147 | 12.2191 | 8.6697 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 0.7447 | 0.7447 | 14.6333 | 10.2358 | 7.5007 | 0.7447 | 9.0987 | 0.2593 | PP submitted, offer due 16/04/2025
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.4591 | 11.9591 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 1.2188 | 5.8558 | 32.1414 | 12.376 | 9.0299 | 5.8558 | 8.9257 | 9.6892 | Offer signed 27/08/2024
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0 | 0 | 7.5611 | 7.5611 | 7.5611 | 0 | 7.4769 | 2.881 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 6.6892 | 18.6392 | 8.441 | 1.3897 | 0.99884 | 8.441 | 1.4212 | 12.0107 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.3598 | 12.9968 | 30.3846 | 5.302 | 3.8852 | 12.9968 | 5.4751 | 12.055 | Offer signed 27/08/2024
GOLBORNE | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 0.62243 | 6.1224 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 4.2925 | 8.9295 | 29.9812 | 10.1559 | 7.2992 | 8.9295 | 7.0494 | 5.6473 | Offer signed 27/08/2024
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.2872 | 14.3872 | 24.7332 | 6.3977 | 4.6679 | 14.3872 | 5.885 | 14.3872 | PP submitted, offer due 12/05/2025
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.226 | 10.226 | 21.0097 | 21.0097 | 16.3318 | 10.226 | 19.5311 | 10.7263 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 8.8093 | 16.9293 | 19.4454 | 3.388 | 2.4719 | 16.9293 | 1.1085 | 9.368 | PP submitted, offer due 12/05/2025
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 5.1213 | 9.7583 | 32.2668 | 15.6719 | 11.2637 | 9.7583 | 11.1508 | 10.8283 | PP submitted, offer due 16/04/2025
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 0 | 3.2261 | 33.5043 | 8.7673 | 6.3013 | 3.2261 | 5.6166 | 0.45951 | Offer with ENW, due to be signed 22/01/2025
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0 | 3.5464 | 21.3921 | 9.1302 | 6.6616 | 3.5464 | 4.1968 | 3.8848 | Offer signed 27/08/2024
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 1.6243 | 10.1549 | 32.3774 | 7.569 | 5.5225 | 10.1549 | 5.7981 | 10.2071 | Offer signed 27/08/2024
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 12.2922 | 16.7922 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 15.7718 | 23.5255 | 55.5263 | 9.9013 | 7.2243 | 23.5255 | 6.8407 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 0 | 13.1505 | 21.0205 | 3.668 | 2.6879 | 13.1505 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 12.0416 | 16.7619 | 7.668 | 1.2625 | 0.90737 | 7.668 | 0.83754 | 7.0779 | Offer signed 27/08/2024
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 0 | 0 | 21.3624 | 10.3438 | 7.5471 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 7.1495 | 11.7865 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0 | 0 | 10.8975 | 10.8975 | 10.8975 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 5.6699 | 10.3069 | 31.6811 | 12.6586 | 9.236 | 10.3069 | 9.5452 | 9.9239 | PP submitted, offer due 12/05/2025
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 10.778 | 15.418 | 30.4539 | 12.3394 | 9.0031 | 15.418 | 9.1946 | 15.552 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 2.82 | 7.12 | 11.2179 | 1.9575 | 1.4344 | 7.12 | 1.4344 | 7.187 | Offer signed 24/12/2024
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 1.4258 | 4.9258 | 15.8004 | 4.9131 | 3.5311 | 4.9258 | 3.4214 | 6.4802 | Offer signed 27/08/2024
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.291 | 6.791 | 13.0026 | 13.0026 | 13.0026 | 6.791 | 13.0026 | 6.7952 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 11.2015 | 15.7015 | 30.5328 | 16.9162 | 12.158 | 15.7015 | 12.0132 | 15.4515 | Offer with ENW, due to be signed 22/01/2025
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 6.8033 | 12.3033 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.1069 | 19.3269 | 3.4123 | 0.56181 | 0.40378 | 3.4123 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.1069 | 19.3269 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 1.0099 | 4.5099 | 24.7522 | 10.2066 | 7.447 | 4.5099 | 7.0425 | 7.7035 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 7.187 | 7.187 | 6.8624 | 1.9575 | 1.4344 | 6.8624 | 1.4344 | 2.695 | Offer signed 24/12/2024
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.2144 | 17.4244 | 29.9937 | 9.0987 | 6.6386 | 17.4244 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 0 | 0 | 31.1274 | 9.5893 | 6.9966 | 0 | 7.1221 | 0 | Offer with ENW, due to be signed 22/01/2025
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0 | 0 | 27.8042 | 4.5095 | 3.2902 | 0 | 3.0681 | 0 | Offer with ENW, due to be signed 22/01/2025
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.44686 | 8.4469 | 13.2972 | 13.2972 | 13.2972 | 8.4469 | 13.2972 | 8.3367 | PP submitted, offer due 12/05/2025
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 12.9453 | 17.0823 | 14.6978 | 11.5227 | 8.2816 | 14.6978 | 9.101 | 17.1039 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.6561 | 14.2931 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 10.1531 | 14.7901 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 6.0399 | 7.1711 | 16.1082 | 2.6125 | 1.9062 | 7.1711 | 1.2885 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 4.5777 | 12.0777 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 3.0994 | 7.7364 | 21.3152 | 5.3818 | 3.868 | 7.7364 | 3.7037 | 4.126 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 6.9262 | 7 | 1.9575 | 1.4344 | 6.9262 | 1.4344 | 7 | Offer signed 24/12/2024
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0.95096 | Offer signed 24/12/2024
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 5.6215 | 8.6289 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Offer signed 24/12/2024
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 2.4484 | 2.4484 | 26.6633 | 7.1331 | 5.2045 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.7551 | 10.8921 | 11.2179 | 1.9575 | 1.4344 | 10.8921 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 3.337 | 6.837 | 11.2179 | 1.9575 | 1.4344 | 6.837 | 1.4344 | 6.5258 | Offer signed 24/12/2024
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 5.5232 | 9.0232 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 0 | 0 | 21.6275 | 18.5454 | 13.5898 | 0 | 17.2503 | 13.3736 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 5.7605 | 10.3975 | 30.3846 | 5.302 | 3.8852 | 10.3975 | 5.4751 | 11.4433 | Offer signed 27/08/2024
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 5.4125 | 17.7125 | 29.3612 | 13.5609 | 9.8944 | 17.7125 | 7.0436 | 17.6125 | PP submitted, offer due 12/05/2025
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 0 | 16.3122 | 21.0205 | 3.668 | 2.6879 | 16.3122 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 9.0341 | 12.6981 | 12.6981 | 12.6981 | 9.0341 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 2.4849 | 6.6249 | 11.2179 | 1.9575 | 1.4344 | 6.6249 | 1.4344 | 4.4053 | PP submitted, offer due 16/04/2025
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 7.3916 | 11.5286 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.3013 | 17.4383 | 29.8132 | 13.332 | 9.7274 | 17.4383 | 7.0436 | 16.5205 | PP submitted, offer due 12/05/2025
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 6.1155 | 28.0218 | 9.404 | 6.7589 | 6.1155 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 2.3127 | 4.8127 | 7 | 1.9575 | 1.4344 | 4.8127 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 12.2191 | 12.2191 | 45.8137 | 8.1615 | 5.8659 | 12.2191 | 1.6009 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.81619 | 2.3162 | 3.1954 | 3.1954 | 3.1954 | 2.3162 | 3.1954 | 2.3112 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 6.1621 | 13.7662 | 13.7662 | 13.7662 | 6.1621 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.1941 | 5.6941 | 3.4566 | 3.4566 | 3.4566 | 3.4566 | 2.8987 | 2.8987 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 0 | 0 | 19.5904 | 18.5454 | 13.5898 | 0 | 19.5904 | 10.2783 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 0 | 0 | 22.1763 | 18.5454 | 13.5898 | 0 | 18.6543 | 13.2545 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 3.5567 | 5.9067 | 19.9589 | 11.3827 | 8.181 | 5.9067 | 8.0695 | 0 | Offer signed 24/12/2024
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 0 | 10.8781 | 31.9515 | 12.5497 | 9.1566 | 10.8781 | 9.0797 | 10.8837 | Offer signed 27/08/2024
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 0 | 31.367 | 6.9395 | 5.0633 | 0 | 4.9077 | 0 | Offer with ENW, due to be signed 11/03/2025
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 0 | 12.5551 | 24.478 | 9.5409 | 6.9613 | 12.5551 | 7.0795 | 15.6051 | Offer signed 27/08/2024
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 2.4484 | 2.4484 | 33.1798 | 8.9114 | 6.5302 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 2.5645 | 14.9594 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 12/05/2025
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.3639 | 8.6289 | 19.6186 | 19.6186 | 19.6186 | 8.6289 | 19.6186 | 0 | Offer signed 24/12/2024
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 2.5861 | 6.0861 | 25.4427 | 13.7701 | 10.047 | 6.0861 | 10.1941 | 6.1719 | Offer with ENW, due to be signed 22/01/2025
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 13.7639 | 21.549 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 3.4504 | 7 | 1.9575 | 1.4344 | 3.4504 | 1.4344 | 4.4466 | Offer signed 24/12/2024
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 0 | 0 | 16.5605 | 16.5605 | 13.5898 | 0 | 16.5605 | 4.0762 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 1.7362 | 5.2362 | 25.0991 | 9.73 | 7.0992 | 5.2362 | 6.9929 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 3.6262 | 12.6498 | 31.2344 | 7.8205 | 5.7061 | 12.6498 | 5.7031 | 10.4658 | Offer with ENW, due to be signed 11/03/2025
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 4.0415 | 4.0415 | 11.2179 | 1.9575 | 1.4344 | 4.0415 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 2.3892 | 6.5262 | 27.2475 | 5.3441 | 3.8992 | 6.5262 | 2.8907 | 9.1882 | Offer with ENW, due to be signed 22/01/2025
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 1.8073 | 7.8073 | 35.3057 | 5.8128 | 4.1778 | 7.8073 | 0.088852 | 0 | Offer signed 24/12/2024
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 0 | 16.7469 | 21.0205 | 3.668 | 2.6879 | 16.7469 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 10.5236 | 12.7606 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.6576 | PP submitted, offer due 16/04/2025
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 3.4276 | 30.0909 | 10.2041 | 7.4452 | 3.4276 | 7.4513 | 1.5496 | Offer with ENW, due to be signed 22/01/2025
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0 | 0 | 7.1061 | 7.1061 | 7.1061 | 0 | 7.1061 | 0 | Offer with ENW, due to be signed 22/01/2025
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 10.1794 | 14.7794 | 24.6386 | 8.3787 | 6.1133 | 14.7794 | 6.5522 | 14.5624 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 8.9475 | 17.6711 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.2476 | 7.1573 | 7.1573 | 7.1573 | 3.2476 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 0 | 0 | 21.3624 | 12.8636 | 9.3856 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 2.4484 | 2.4484 | 26.9066 | 4.43 | 3.1839 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 8.9576 | 11.7574 | 14.6978 | 14.6978 | 14.6978 | 11.7574 | 18.0835 | 11.4916 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 10.7378 | 15.3778 | 30.1883 | 10.3371 | 7.5423 | 15.3778 | 7.4802 | 14.0754 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 7.47 | 15.4877 | 2.5499 | 1.8327 | 7.47 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 5.5874 | 9.0874 | 11.2179 | 1.9575 | 1.4344 | 9.0874 | 1.4344 | 0 | Offer signed 27/08/2024
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 3.2499 | 6.7499 | 11.2179 | 1.9575 | 1.4344 | 6.7499 | 1.4344 | 5.0297 | PP submitted, offer due 16/04/2025
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 2.2581 | 5.7581 | 11.2179 | 1.9575 | 1.4344 | 5.7581 | 1.4344 | 8.9507 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 8.3041 | 12.1041 | 2.5513 | 0.44197 | 0.31765 | 2.5513 | 0.31765 | 2.6844 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 0.76382 | 4.2638 | 23.7167 | 9.179 | 6.6973 | 4.2638 | 5.8695 | 0 | Offer with ENW, due to be signed 11/03/2025
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 4.0674 | 7 | 1.9575 | 1.4344 | 4.0674 | 1.4344 | 3.7702 | Offer signed 24/12/2024
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 14.8904 | 21.4377 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.3845 | 6.6985 | 27.9116 | 12.685 | 9.117 | 6.6985 | 9.1199 | 4.5253 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.6392 | 31.5971 | 10.3001 | 7.5153 | 2.6392 | 7.5673 | 1.6732 | Offer with ENW, due to be signed 22/01/2025
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 9.235 | 13.872 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 2.0189 | 6.6558 | 11.2179 | 1.9575 | 1.4344 | 6.6558 | 1.4344 | 8.7054 | PP submitted, offer due 16/04/2025
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.642 | 14.262 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 1.4658 | 5.6058 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 12/05/2025
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 2.4484 | 2.4484 | 31.0839 | 8.9114 | 6.5302 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 0 | 3.8322 | 3.8322 | 3.8322 | 0 | 3.8322 | 2.0546 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0 | 0 | 15.0523 | 15.0523 | 13.5898 | 0 | 15.0523 | 7.0631 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.7563 | 15.5143 | 15.6356 | 5.302 | 3.8852 | 15.5143 | 1.511 | 1.511 | Offer signed 27/08/2024
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 1.9905 | 1.9905 | 12.0025 | 8.9114 | 6.5302 | 1.9905 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 8.7634 | 12.9004 | 28.3704 | 10.9651 | 8.0074 | 12.9004 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 22.1763 | 6.3864 | 4.59 | 0 | 3.841 | 8.6565 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 16.5236 | 16.5236 | 13.5898 | 0 | 14.4183 | 10.2752 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.3747 | 22.8902 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 10.3038 | 14.9408 | 8.1623 | 1.3439 | 0.96586 | 8.1623 | 0.56343 | 4.7615 | Offer with ENW, due to be signed 22/01/2025
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 7.508 | 11.008 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 9.31 | Offer with ENW, due to be signed 11/03/2025
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 2.2613 | 7.2013 | 11.2179 | 1.9575 | 1.4344 | 7.2013 | 1.4344 | 10.0382 | PP submitted, offer due 16/04/2025
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 0 | 0 | 30.5974 | 12.4768 | 9.1034 | 0 | 9.1327 | 0 | Offer with ENW, due to be signed 22/01/2025
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 1.9732 | 5.4732 | 0.37436 | 0.065324 | 0.047869 | 0.37436 | 1.4344 | 5.886 | Offer signed 27/08/2024
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 8.7868 | 13.4238 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 13.3772 | 21.3337 | 7.8607 | 1.2942 | 0.93016 | 7.8607 | 0.84345 | 7.1279 | PP submitted, offer due 12/05/2025
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0 | 8.7176 | 19.6031 | 19.6031 | 19.6031 | 8.7176 | 19.6031 | 8.983 | PP submitted, offer due 12/05/2025
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 7.9823 | 12.1193 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 1.4954 | 10.4954 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 12/05/2025
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 0 | 14.0343 | 29.5281 | 8.497 | 6.1997 | 14.0343 | 6.0414 | 15.0117 | Offer with ENW, due to be signed 11/03/2025
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 8.5018 | 22.9057 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 7.7571 | 11.5571 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 0 | 0 | 31.2648 | 9.1528 | 6.6781 | 0 | 6.7371 | 0 | Offer with ENW, due to be signed 22/01/2025
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 9.1275 | 11.1075 | 11.2179 | 1.9575 | 1.4344 | 11.1075 | 1.4344 | 6.9765 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 6.697 | 10.197 | 23.6228 | 13.2344 | 9.5118 | 10.197 | 9.4181 | 10.8112 | Offer with ENW, due to be signed 22/01/2025
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 11.2011 | 15.7011 | 26.8965 | 10.2358 | 7.5007 | 15.7011 | 9.0987 | 15.8281 | PP submitted, offer due 16/04/2025
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 4.0415 | 4.0415 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 11.301 | 15.938 | 30.2268 | 11.7728 | 8.5898 | 15.938 | 8.77 | 17.138 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 4.6586 | 9.2956 | 32.1779 | 7.9726 | 5.8171 | 9.2956 | 5.8553 | 6.3816 | Offer signed 24/12/2024
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 5.0473 | 12.6073 | 30.2531 | 12.328 | 8.9948 | 12.6073 | 8.8549 | 17.2513 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.2872 | 14.3872 | 24.7332 | 11.0961 | 8.096 | 14.3872 | 9.5083 | 14.3872 | PP submitted, offer due 12/05/2025
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 0 | 0.62514 | 11.2179 | 1.9575 | 1.4344 | 0.62514 | 1.4344 | 0 | Offer signed 27/08/2024
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 8.6009 | 9.0009 | 43.9949 | 11.7845 | 8.4697 | 9.0009 | 8.7443 | 5.7413 | Offer signed 24/12/2024
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 6.6019 | 19.3019 | 34.9192 | 12.5565 | 9.1616 | 19.3019 | 8.8192 | 17.3639 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.6415 | 15.2785 | 30.169 | 15.9255 | 11.6197 | 15.2785 | 11.7382 | 14.2835 | PP submitted, offer due 12/05/2025
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 0 | 0 | 30.3545 | 9.8399 | 7.1795 | 0 | 7.0914 | 0 | Offer with ENW, due to be signed 22/01/2025
RIBBLESDALE T13 & RIBBLESDALE T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 1.934 | 4.684 | 22.1282 | 16.353 | 11.7532 | 4.684 | 11.8923 | 1.683 | PP submitted, offer due 12/05/2025
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 4.0415 | 4.0415 | 11.2179 | 1.9575 | 1.4344 | 4.0415 | 1.4344 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 9.003 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 8.7641 | 8.8484 | 1.4568 | 1.047 | 8.7641 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 18.5255 | 31.5255 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 0 | 14.7322 | 21.0205 | 3.668 | 2.6879 | 14.7322 | 0 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 0 | 0 | 24.0007 | 10.8422 | 7.7925 | 0 | 7.5834 | 0 | Offer with ENW, due to be signed 22/01/2025
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 0 | 3.109 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 16/04/2025
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 8.9049 | 13.5419 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 11.4457 | 16.0857 | 31.0489 | 8.4662 | 6.1772 | 16.0857 | 6.5677 | 14.7385 | PP submitted, offer due 16/04/2025
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 1.5401 | 1.5401 | 12.01 | 12.01 | 12.01 | 1.5401 | 12.01 | 1.3941 | PP submitted, offer due 16/04/2025
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 11.68 | 16.18 | 30.3 | 17.8474 | 12.8273 | 16.18
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 8.2924 | 12.7924 | 30.2683 | 8.9772 | 6.5784 | 12.7924 | 7.2924 | 14.3266 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.1832 | 3.6832 | 6.4667 | 1.9575 | 1.4344 | 3.6832 | 1.4344 | 3.6656 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0 | 0.36018 | 1.9438 | 1.9438 | 1.4344 | 0.36018 | 1.4344 | 1.1732 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 9.8759 | 19.5532 | 19.5532 | 19.3747 | 9.8759 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0 | 0 | 4.9054 | 4.9054 | 4.9054 | 0 | 4.9054 | 1.1883 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.28601 | 7.786 | 13.3716 | 13.3716 | 13.3716 | 7.786 | 13.3716 | 7.6618 | PP submitted, offer due 12/05/2025
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.0585 | 7.4085 | 32.0548 | 26.424 | 18.9915 | 7.4085 | 18.9995 | 5.2353 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 4.228 | 9.728 | 32.1479 | 10.7396 | 7.8359 | 9.728 | 8.0106 | 5.397 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 0 | 0 | 12.2325 | 12.2325 | 12.2325 | 0 | 12.2325 | 7.0318 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 9.6466 | 14.2836 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.139 | 23.7298 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 16.119 | 38.4576 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 4.4324 | 9.0694 | 11.2179 | 1.9065 | 1.3702 | 9.0694 | 1.3976 | 7.809 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 0 | 0 | 22.1763 | 18.5454 | 13.5898 | 0 | 17.7881 | 13.3736 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 5.3535 | 7.3535 | 14.6978 | 14.6978 | 11.7821 | 7.3535 | 12.7115 | 7.3459 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 6.865 | 11.502 | 0.37436 | 0.065324 | 0.047869 | 0.37436 | 1.4344 | 11.2179 | Offer signed 27/08/2024
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 8.8832 | 8.8832 | 11.2179 | 1.9575 | 1.4344 | 8.8832 | 1.4344 | 0 | PP submitted, offer due 09/04/2025
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.4307 | 18.2303 | 29.4531 | 11.4404 | 8.2224 | 18.2303 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.514 | 6.651 | 11.2179 | 1.9575 | 1.4344 | 6.651 | 1.4344 | 0 | PP submitted, offer due 09/04/2025
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 5.2005 | 5.2005 | 11.2179 | 1.9575 | 1.4344 | 5.2005 | 1.4344 | 5.2215 | Offer signed 24/12/2024
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 25.7295 | 32.7295 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 6.7756 | 10.2756 | 23.6188 | 13.2188 | 9.6448 | 10.2756 | 4.1691 | 9.6296 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 2.5645 | 18.7784 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, offer due 12/05/2025
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 6.2683 | 10.8683 | 16.6911 | 2.7071 | 1.9751 | 10.8683 | 2.1114 | 6.2955 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 9.1032 | 12.6032 | 23.0658 | 9.7394 | 7.1062 | 12.6032 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 11.6132 | 16.2502 | 29.2752 | 10.5844 | 7.7227 | 16.2502 | 7.7148 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 7.1664 | 10.6664 | 11.2179 | 1.9575 | 1.4344 | 10.6664 | 1.4344 | 10.0664 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 13.7705 | 18.2303 | 30.1228 | 12.8909 | 9.4056 | 18.2303 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.1817 | 10.6817 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0 | 0 | 2.6844 | 0.44197 | 0.31765 | 0 | 1.9914 | 1.9914 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 5.2912 | 9.4282 | 20.7477 | 3.365 | 2.4552 | 9.4282 | 2.4384 | 6.5078 | PP submitted, offer due 12/05/2025
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 5.0081 | 12.0081 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 9.7731 | 26.7731 | 25.8967 | 4.2637 | 3.0644 | 25.8967 | 2.782 | 23.5098 | PP submitted, offer due 12/05/2025
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.6986 | 18.1986 | 30.2092 | 14.931 | 10.7312 | 18.1986 | 10.853 | 18.1986 | Offer signed 24/12/2024
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 7.1554 | 11.7924 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 8.916 | 13.053 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0 | 0 | 20.8292 | 7.469 | 5.3681 | 0 | 0.31765 | 2.6844 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 2.9681 | 13.6681 | 29.77 | 10.0811 | 7.3555 | 13.6681 | 7.3789 | 14.5981 | Offer signed 24/12/2024
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 17.3341 | 26.4 | 8 | 1.9575 | 1.4344 | 8
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 8.6442 | 11.7812 | 11.2179 | 1.9109 | 1.3734 | 11.2179 | 0.31765 | 2.6844 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 2.4484 | 2.4484 | 33.4932 | 8.9114 | 6.5302 | 2.4484 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 3.6262 | 11.8269 | 22.3705 | 7.7165 | 5.6302 | 11.8269 | 5.7122 | 14.3365 | Offer with ENW, due to be signed 11/03/2025
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 6.2399 | 11.4899 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | PP submitted, offer due 16/04/2025
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 20.0999 | 20.0999 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 24/12/2024
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 7.3748 | 11.5118 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 5.727 | 8.727 | 16.3552 | 9.9112 | 7.1234 | 8.727 | 7.6223 | 7.75 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 1.6788 | 6.3158 | 11.2179 | 1.9575 | 1.4344 | 6.3158 | 1.4344 | 9.7198 | Offer signed 24/12/2024
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 0 | 6.8611 | 22.0084 | 11.0686 | 7.9552 | 6.8611 | 8.1328 | 6.6945 | Offer signed 27/08/2024
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 3.6262 | 14.9211 | 28.9446 | 7.919 | 5.7779 | 14.9211 | 5.7691 | 14.4783 | Offer with ENW, due to be signed 11/03/2025
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 5.1043 | 25.5112 | 8.2669 | 6.0318 | 5.1043 | 4.6312 | 4.9475 | Offer with ENW, due to be signed 22/01/2025
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.4371 | 10.9371 | 11.2179 | 1.9575 | 1.4344 | 10.9371 | 1.4344 | 10.9371 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 5.8835 | 10.5205 | 31.4551 | 7.9788 | 5.8215 | 10.5205 | 5.5739 | 0 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 0 | 0 | 21.3624 | 12.6314 | 9.2162 | 0 | 0 | 0 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 14.6569 | 19.2939 | 29.365 | 13.0587 | 9.528 | 19.2939 | 9.344 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 2.4011 | 2.4011 | 28.4979 | 12.4466 | 8.9456 | 2.4011 | 1.3561 | 10.6051 | Offer signed 27/08/2024
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 13.7613 | 18.3983 | 30.177 | 12.7138 | 9.2763 | 18.3983 | 8.8768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 12.7289 | 17.3659 | 30.2639 | 13.449 | 9.8127 | 17.3659 | 10.1945 | 7.7239 | PP submitted, offer due 12/05/2025
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7897 | 10.7897 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 8.6933 | Offer with ENW, due to be signed 11/03/2025
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0 | 4.4346 | 11.4016 | 1.8772 | 1.3492 | 4.4346 | 0.088852 | 0 | Offer signed 24/12/2024
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 5.5213 | 8.6576 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 8.8247 | 13.4617 | 28.3048 | 8.2116 | 5.9018 | 13.4617 | 5.5392 | 11.0853 | PP submitted, offer due 12/05/2025
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 2.5842 | 11.7212 | 10.244 | 1.9575 | 1.4344 | 10.244 | 1.4344 | 10.576 | Offer with ENW, due to be signed 11/03/2025
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 5.5937 | 23.0587 | 19.958 | 14.3442 | 5.5937 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 4.791 | 8.291 | 23.9575 | 14.5169 | 10.4336 | 8.291 | 10.3146 | 9.0214 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 5.0644 | 6.5644 | 10.5081 | 4.6411 | 3.3863 | 6.5644 | 3.1391 | 5.9064 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0 | 2.2585 | 7 | 1.9575 | 1.4344 | 2.2585 | 1.4344 | 0.21045 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 9.363 | 14 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.2606 | 5.7606 | 25.3471 | 13.0354 | 9.511 | 5.7606 | 9.2635 | 4.6017 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 6.9548 | 11.0918 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 5.1333 | 8.6333 | 8 | 1.9575 | 1.4344 | 8 | 1.4344 | 5.768 | Offer with ENW, due to be signed 11/03/2025
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 9.8759 | 30.4268 | 20.8382 | 14.9768 | 9.8759 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 5.4547 | 8.9547 | 18.0363 | 6.6838 | 4.8767 | 8.9547 | 2.1791 | 7.5047 | Offer with ENW, due to be signed 22/01/2025
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.7832 | 6.2832 | 10.244 | 1.9575 | 1.4344 | 6.2832 | 1.4344 | 6.0832 | Offer with ENW, due to be signed 11/03/2025
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 8.8832 | 8.8832 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | PP submitted, offer due 09/04/2025
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 6.0486 | 9.5486 | 24.1055 | 14.3413 | 10.4638 | 9.5486 | 10.5673 | 8.8316 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0 | 0 | 30.1487 | 14.0013 | 10.063 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 1.0391 | 1.0391 | 11.2179 | 1.9575 | 1.4344 | 1.0391 | 1.5151 | 2.7595 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 1.0021 | 4.5021 | 8 | 1.9575 | 1.4344 | 4.5021 | 1.4344 | 0.86929 | Offer with ENW, due to be signed 11/03/2025
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 0 | 0 | 10.7443 | 1.769 | 1.2714 | 0 | 1.0921 | 0 | Offer with ENW, due to be signed 22/01/2025
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 10.3982 | 14.3982 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 8.8855 | 13.5225 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 1.6243 | 11.9477 | 26.1692 | 10.8691 | 7.9304 | 11.9477 | 7.7377 | 8.7753 | Offer signed 27/08/2024
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0 | 0 | 30.4446 | 15.2561 | 10.9649 | 0 | 5.1053 | 5.1053 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 6.5082 | 12.8478 | 12.8478 | 12.8478 | 6.5082 | 0 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 52.9004 | 70.9004 | 142.4601 | 46.9336 | 70.9004 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 14.709 | 26.709 | 91.3244 | 27.6584 | 26.709 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Offer signed 24/12/2024
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 53.2922 | 71.2922 | 149.5819 | 49.1319 | 71.2922 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | PP submitted, offer due 16/04/2025
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 8.6289 | 8.6289 | 119.9397 | 27.7907 | 8.6289 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Offer signed 24/12/2024
BARROW | 33 | HARKER | 319709 | 470489 | 37.4738 | 63.4738 | 48.9366 | 8.8779 | 48.9366 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
BARTON | 33 | CARRINGTON | 376758 | 397174 | 36.9135 | 56.5087 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | PP submitted, offer due 16/04/2025
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 12.2191 | 12.2191 | 54.6806 | 23.1425 | 12.2191 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 36.8046 | 36.8046 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 37.2466 | 37.2466 | 68.8709 | 39.1204 | 37.2466 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 40.2499 | 41.0899 | 119.4893 | 35.0571 | 41.0899 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 0 | 28.0306 | 152.6811 | 48.373 | 28.0306 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 17.4431 | 30.1353 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Offer signed 24/12/2024
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 63.7996 | 63.7996 | 80.2594 | 29.5022 | 63.7996 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
BURY | 33 | KEARSLEY | 380272 | 411184 | 29.413 | 29.413 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Offer signed 24/12/2024
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 2.4011 | 2.4011 | 88.4788 | 44.9372 | 2.4011 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Offer signed 27/08/2024
CARLISLE | 33 | HARKER | 338655 | 556583 | 19.744 | 40.944 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 10.4417 | 31.4417 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | PP submitted, offer due 16/04/2025
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 44.2698 | 44.2698 | 103.112 | 37.5854 | 44.2698 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 2.4484 | 2.4484 | 48.578 | 8.8128 | 2.4484 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 35.7503 | 35.7503 | 0.3561 | 0.064602 | 0.3561 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Offer signed 27/08/2024
EGREMONT | 33 | HARKER | 301070 | 513074 | 31.4628 | 31.4628 | 14.6978 | 14.6978 | 14.6978 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 0 | 6.7308 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Offer signed 24/12/2024
GOLBORNE | 33 | BOLD | 360607 | 397690 | 34.1175 | 52.1175 | 59.7732 | 10.8438 | 52.1175 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 23.5255 | 23.5255 | 84.0206 | 29.7947 | 23.5255 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 36.9511 | 54.9511 | 137.0032 | 36.7708 | 54.9511 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 30.1396 | 92.1396 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Offer signed 27/08/2024
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 38.6422 | 52.4422 | 69.8986 | 21.1066 | 52.4422 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | PP submitted, offer due 12/05/2025
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 31.6358 | 31.6358 | 28.9024 | 5.2434 | 28.9024 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Offer signed 27/08/2024
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 25.9858 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Offer signed 24/12/2024
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 9.8759 | 108.9064 | 28.1832 | 9.8759 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 1.0391 | 1.0391 | 10.6707 | 1.9358 | 1.0391 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 11.5793 | 26.5433 | 124.2442 | 32.9142 | 26.5433 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 7.0144 | 25.0144 | 149.1089 | 39.0159 | 25.0144 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 0 | 47.3938 | 19.9951 | 3.6274 | 19.9951 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 18.2303 | 18.2303 | 42.8677 | 40.2907 | 18.2303 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 8.8832 | 8.8832 | 10.6707 | 1.9358 | 8.8832 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | PP submitted, offer due 09/04/2025
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 17.3341 | 42.5341 | 7.6923 | 1.9358 | 7.6923 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
NELSON | 33 | PADIHAM | 385989 | 438643 | 2.5645 | 23.9773 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | PP submitted, offer due 12/05/2025
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 20.5875 | 20.5875 | 53.1931 | 53.1931 | 20.5875 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Offer signed 27/08/2024
ORRELL | 33 | KIRKBY | 352784 | 404565 | 0 | 17.647 | 104.8901 | 44.0239 | 17.647 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Offer signed 27/08/2024
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 13.3772 | 47.239 | 139.7763 | 29.8491 | 47.239 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | PP submitted, offer due 12/05/2025
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 0 | 0 | 21.3624 | 21.3624 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
PENRITH | 33 | HUTTON | 349996 | 530398 | 0 | 0 | 22.1763 | 18.3403 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 4.0415 | 4.0415 | 10.6707 | 1.9358 | 4.0415 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 34.5802 | 52.8765 | 145.8409 | 32.7575 | 52.8765 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 76.0858 | 112.0858 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 48.2311 | 60.2311 | 94.6521 | 40.7553 | 60.2311 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 42.092 | 53.6903 | 106.8182 | 53.3765 | 53.6903 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | PP submitted, offer due 12/05/2025
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 16.134 | 93.1126 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
SALE | 33 | CARRINGTON | 378726 | 392892 | 24.5357 | 24.5357 | 78.4545 | 48.3208 | 24.5357 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | PP submitted, offer due 16/04/2025
SANDGATE | 33 | HARKER | 321492 | 468870 | 37.4738 | 63.4738 | 97.8537 | 17.7522 | 63.4738 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SHAP | 33 | HUTTON | 356910 | 513357 | 0 | 0 | 22.1763 | 22.1763 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
SIDDICK | 33 | HARKER | 300332 | 530823 | 38.0907 | 82.1907 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 22.9057 | 22.9057 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
STAINBURN | 33 | HARKER | 302535 | 529330 | 38.0907 | 82.1907 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 3.6262 | 50.253 | 131.4503 | 33.8261 | 50.253 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 100.0382 | 142.9777 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Offer signed 27/08/2024
THORNTON | 33 | STANAH | 334559 | 443368 | 12.1341 | 24.1341 | 26.8965 | 10.1226 | 24.1341 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | PP submitted, offer due 16/04/2025
ULVERSTON | 33 | HARKER | 327495 | 477808 | 31.1808 | 31.1808 | 35.2954 | 22.0407 | 31.1808 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 0 | 0 | 88.1369 | 16.2796 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | Offer with ENW, due to be signed 22/01/2025
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 14.8345 | 51.3345 | 9.85 | 1.9358 | 9.85 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | Offer with ENW, due to be signed 11/03/2025
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 19.8801 | 19.8801 | 88.0127 | 24.9867 | 19.8801 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Offer signed 24/12/2024
WIGAN | 33 | KIRKBY | 358343 | 404626 | 1.6243 | 40.6243 | 87.9264 | 35.3717 | 40.6243 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Offer signed 27/08/2024
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0 | 0 | 53.4316 | 20.6575 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date

## 6) GSP Demand Headroom Data
GSP Headroom
Substation | GSP | Voltage (kV) | GSP Group | GSP Coordinates |  | Demand Headroom (MVA) |  | Battery Storage Headroom N-0 -(MW)
|  |  |  | Easting | Northing | Firm (non inverter based) | Non Firm (inverter based)
Bold GSP (132) | BOLD | 132 | BOLD | 353959 | 393258 | -139.4996 | -139.4996 | -99.1396 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en
Bredbury (132) | BREDBURY | 132 | BREDBURY | 391365 | 390944 | 132.567 | 148.647 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en
Carrington GSP (132) | CARRINGTON | 132 | CARRINGTON | 372952 | 393301 | -50.1712 | 102.8288 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en
Harker / Hutton GSP (132) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | 132 | HARKER / HUTTON | 338285 | 561159 | -602.0618 | -602.0618 | -1371.8147 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en
Heysham GSP (132) | HEYSHAM | 132 | HEYSHAM | 341889 | 460007 | 184.7123 | 184.7123 | -69.2211 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en
Kearsley GSP (132) | KEARSLEY | 132 | KEARSLEY | 376283 | 404800 | -0.67148 | 136.5485 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en
Padiham (132) | PADIHAM | 132 | PADIHAM | 378522 | 433196 | -252.1956 | -252.1956 | -271.5158 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en
Penwortham East / Rochdale SGT 1 GSP (132) | PENWORTHAM EAST/ROCHDALE | 132 | PENWORTHAM EAST / ROCHDALE | 350213 | 428032 | 324.9553 | 343.7053 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en
Penwortham West / Stanah GSP (132) | PENWORTHAM WEST/STANAH | 132 | PENWORTHAM WEST / STANAH | 350200 | 428029 | 269.5014 | 269.5014 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en
Rochdale GSP (132) | ROCHDALE | 132 | ROCHDALE | 385789 | 413832 | 127.48 | 127.48 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en
South Manchester GSP (132) | SOUTH MANCHESTER | 132 | SOUTH MANCHESTER | 381823 | 391734 | 185.7409 | 185.7409 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en
Stalybridge GSP (132) | STALYBRIDGE | 132 | STALYBRIDGE | 397172 | 399496 | 101.5244 | 198.4244 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en
Washway Farm / Kirkby GSP (132) | Washway Farm GSP / Kirkby GSP GROUP | 132 | WASHWAY FARM / KIRKBY | 345822 | 407637 | -126.3446 | -126.3446 | -34.7305 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en
Whitegate GSP (132) | WHITEGATE | 132 | WHITEGATE | 389202 | 403745 | 176.2703 | 280.0703 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en

## 7)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | 0 | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 282 | 0 | C | 0 | 426.2 | 3 | Offer with ENW, due to be signed 22/01/2025
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 0 | 0 | C | 4 | 199 | 5.13 | PP submitted, offer due 16/04/2025
HARKER | HARKER | 765.4 | 88 | 0 | 931.8 | 0 | D | 504.6 | 1785.2 | 0 | Offerwith ENW , due to be signed 12/05/2025. Another PP submitted, offer due 28/04/2025
HUTTON | HUTTON | 47.9 | 53 | 0 | 151 | 0 | D | 233.8 | 251.9 | 0 | Offer signed 11/03/2025. Another PP submitted,offer due 12/05/2025
HEYSHAM | HEYSHAM | 292.6 | 0 | 109 | 21.5 | 0 | C | 24 | 423.1 | 0 | Offer with ENW, due to be signed 14/01/2025. Another submission made, awaiting Clock start date.
KEARSLEY | KEARSLEY | 57.9 | 264.7 | 11 | 35 | 0 | C | 0 | 368.6 | 3 | Offer signed 24/12/2024
KIRKBY | KIRKBY | 6 | 146.4 | 0 | 80.9 | 0 | D | 0 | 233.3 | 3 | Offer signed 27/08/2024
MACCLESFIELD | MACCLESFIELD | 27.9 | 30 | 0 | 0 | 0 | C | 7.5 | 57.9 | 2.57 | PP submitted, offer due 09/04/2025
PADIHAM | PADIHAM | 35.5 | 135.1 | 219.9 | 164.9 | 0 | D | 7 | 555.4 | TBC | PP submitted, offer due 12/05/2025
PENWORTHAM | PENWORTHAM | 187.9 | 601.1 | 67.6 | 109.2 | 144 | D | 184.9 | 1109.8 | 9.21 | Offer signed 23/01/2025. Another offer with ENW, due to be signed 16/04/2025. Another parrallel submission made,offer due 08/04/2025.Another submission made, awaiting Clock start date
ROCHDALE | ROCHDALE | 204.1 | 179.1 | 35 | 191.3 | 0 | C | 184.9 | 639.5 | 1.92 | Offer with ENW, due to be signed 11/05/2025.Another PP submitted,offer due 06/05/25
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 649.7 | 0 | C | 0 | 753.2 | 0 | Offer with ENW, due to be signed 11/03/2025
STALYBRIDGE | STALYBRIDGE | 58.3 | 236.8 | 0 | 50 | 0 | C | 0 | 345.1 | 0.591 | Offer signed 27/08/2024
STANAH | STANAH | 195.9 | 142 | 0 | 0 | 0 | C | 50 | 387.9 | 3.01 | PP submitted, offer due 16/04/2025
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 51.9 | 0 | D | 0 | 161 | 3 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WHITEGATE | WHITEGATE | 32 | 219.8 | 0 | 128.2 | 0 | C | 0 | 380 | 3.09 | Offers with ENW, due to be signed 28/08/2024 - now extended to address queries
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application. D. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New GSPs have now been trigged by the latest Project progression return by ESO.